## Protocol Explanation
Write Format
Device Address | Function Code | Start Address |  | Write Register No. |  | Write Byte No. | Data to write in |  |  |  |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | 1 Byte | Hi Byte 1 | Low Byte 1 | … | Hi Byte N | Low Byte N | Low Byte | Hi Byte
Broadcast Address:0x00; Device Address:1-247 | Write Function Code:0x10 | [5 empty] | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explanation. For example, sequence to send a 32bits data: byte3, byte2, byte1, byte0 |  |  |  |  | Modbus-CRC16
Response Format of Write
Device Address | Function Code | Start Address |  | Write Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Slave Address | Write Function Code:0x10 |  |  |  |  | Modbus-CRC16
Read Format
Device Address | Function Code | Start Address |  | Read Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Device Address:1-247 | ReadFunction Code:0x03 |  |  |  |  | Modbus-CRC16
Response Format of Read
Device Address | Function Code | Data Byte No. | Response register data |  |  |  |  | CRC
1 Byte | 1 Byte | 1 Byte | Hi Byte 1 | Low Byte 1 | … | Hi Byte N | Low Byte N | Low Byte | Hi Byte
Slave Address | ReadFunction Code:0x03 |  | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explaination. For example , sequence to send a 32bits data: byte3,byte2,byte1,byte0 |  |  |  |  | Modbus-CRC16
Abnormal Response
Device Address | Function Code | Error Code |  | CRC
1 Byte | 1 Byte | 1 Byte |  | Low Byte | Hi Byte
Slave Address | Abnormal Function Code:0x90 | See Error Code List |  | Modbus-CRC16
Read and write explanation
Value | Name | Explanation
R | Readable | Readable registers
W | Writable | Writable registers
V | Volatile | Variable registers, support frequent write operations

## Registers
| Register address | Field | Type | Accuracy | Unit | Min | Max | Read/Write | Remarks | User
General
| 0040 | AddressMask_General1 | U64 |  |  |  |  | R | The validity of 64 addresses above the address range (including the address of this partition) corresponding to each bit of this partition. 0 means invalid; 1 means valid. | End User
| 0041 | [8 empty] | End User
| 0042 | [8 empty] | End User
| 0043 | [8 empty] | End User
| 0044 | Modbus_Protocol_Version | BCD16 |  |  | 1.06 | 99.99 | R | Version number of this protocol. The protocol version number corresponds to the version number in the cover of this protocol. Bits 0-7 represent the minor version number, bits 0-3 represent the low version number, and bits 4-7 represent the high version number. Bits 8-15 represent the major version number, of which bits 8-11 represent the low-order version number, and bits 12-15 represent the high-order version number. Example: The value 0x1234 indicates that the protocol version number is 12.34 | End User
| 0045 | COMM_MCU_Code | ASCII |  |  |  |  | R | Communication chip code. Refer to the chip coding specification, not open to modify. Example: 0x4730 means "G0" | End User
| 0046 | CTRL1_MCU_Code | ASCII |  |  |  |  | R | No. 1 control chip code. Refer to the chip coding specification, not open to Modify. Example: 0x4730 means "G0" | End User
| 0047 | CTRL2_MCU_Code | ASCII |  |  |  |  | R | No. 2 control chip code name. Refer to the chip coding specification, not open to Modify. Example: 0x4730 means "G0" | End User
| 0048 | MCU_Code_Rsvd1
| 0049 | MCU_Code_Rsvd2
| 004A | MCU_Code_Rsvd3
| 004B | MCU_Code_Rsvd4
| 004C | MCU_Code_Rsvd5
| 004D | MCU_Code_Rsvd6
| 004E | MCU_Code_Rsvd7
| 004F | MCU_Code_Rsvd8
| 0050 | MCU_Code_Rsvd9
| 0051 | MCU_Code_Rsvd10
| 0052 | Protocol_ARM-DSPM |  |  |  | 0 | 0xFFFF | R | Protocol version number between ARM and DSP The high 8 bits correspond to the protocol version number of ARM-DSPM, and the low 8 bits correspond to the protocol version number of DSPM-ARM Example: 0x0102 means the protocol version number of ARM-DSPM is 001, and the protocol version number of DSPM-ARM is 002 | End User
| 0053 | Protocol_Version_Rsvd2
| 0054 | Protocol_Version_Rsvd3
| 0055 | Protocol_Version_Rsvd4
| 0056 | Protocol_Version_Rsvd5
| 0057 | Protocol_Version_Rsvd6
| 0058 | Protocol_Version_Rsvd7
| 0059 | Protocol_Version_Rsvd8
| 005A | Protocol_Version_Rsvd9
| 005B | Protocol_Version_Rsvd10
| 005C | Protocol_Version_Rsvd11
| 005D | Protocol_Version_Rsvd12
| 005E | Protocol_Version_Rsvd13
| 005F | Protocol_Version_Rsvd14
| 0060 | Protocol_Version_Rsvd15
| 0061 | Protocol_Version_Rsvd16
| 0062 | Protocol_Version_Rsvd17
| 0063 | Protocol_Version_Rsvd18
| 0064 | Protocol_Version_Rsvd19
| 0065 | Protocol_Version_Rsvd20
0066
0067
0068
0069
006A
006B
006C
006D
006E
006F
0070
0071
0072
0073
0074
0075
0076
0077
0078
0079
007A
007B
007C
007D
| 007E | Customer ID_0 | [5 empty] | RW | Distinguish the ID used by different customers, refer to the customer coding specification Customer ID_0: Used to mark the customer ID, such as the default SofarSolar is 0x0000. Example: Trina 0x0001, Skyworth 0x0002, etc. | End User
| 007F | Customer ID_1 | [5 empty] | RW | Customer ID_1: Alternate expansion | End User
Real time data (0x0400-0x07FF)
System info (0x0400-0x047F)
| 0400 | AddressMask_Realtime_SysInfo1 | U64 |  |  |  |  | R | The validity of 64 addresses above the address range (including the address of this partition) corresponding to each bit of this partition. 0 means invalid; 1 means valid. | End User
| 0401 | [8 empty] | End User
| 0402 | [8 empty] | End User
| 0403 | [8 empty] | End User
| 0404 | SysState | U16 |  |  |  |  | R | Operating status 0: waiting state 1: Detection status 2: Grid-connected status 3: Emergency power supply status 4: Recoverable fault state 5: Permanent fault status 6: Upgrade status 7: Self-charging status 8：SVG status 9：PID status | End User
| 0405 | Fault1 | U16 |  |  |  |  | R | Fault information table 1 | End User
| 0406 | Fault2 | U16 |  |  |  |  | R | Fault information table 2 | End User
| 0407 | Fault3 | U16 |  |  |  |  | R | Fault information table 3 | End User
| 0408 | Fault4 | U16 |  |  |  |  | R | Fault information table 4 | End User
| 0409 | Fault5 | U16 |  |  |  |  | R | Fault information table 5 | End User
| 040A | Fault6 | U16 |  |  |  |  | R | Fault information table 6 | End User
| 040B | Fault7 | U16 |  |  |  |  | R | Fault information table 7 | End User
| 040C | Fault8 | U16 |  |  |  |  | R | Fault information table 8 | End User
| 040D | Fault9 | U16 |  |  |  |  | R | Fault information table 9 | End User
| 040E | Fault10 | U16 |  |  |  |  | R | Fault information table 10 | End User
| 040F | Fault11 | U16 |  |  |  |  | R | Fault information table 11 | End User
| 0410 | Fault12 | U16 |  |  |  |  | R | Fault information table 12 | End User
| 0411 | Fault13 | U16 |  |  |  |  | R | Fault information table 13 | End User
| 0412 | Fault14 | U16 |  |  |  |  | R | Fault information table 14 | End User
| 0413 | Fault15 | U16 |  |  |  |  | R | Fault information table 15 | End User
| 0414 | Fault16 | U16 |  |  |  |  | R | Fault information table 16 | End User
| 0415 | Fault17 | U16 |  |  |  |  | R | Fault information table 17 | End User
| 0416 | Fault18 | U16 |  |  |  |  | R | Fault information table 18 | End User
| 0417 | Countdown | U16 | 1 | seconds |  |  | R | Power-on countdown | End User
| 0418 | Temperature_Env1 | I16 | 1 | ℃ |  |  | R | Ambient temperature 1 | End User
| 0419 | Temperature_Env2 | I16 | 1 | ℃ |  |  | R | Ambient temperature 2 | End User
| 041A | Temperature_HeatSink1 | I16 | 1 | ℃ |  |  | R | Radiator temperature 1 | End User
| 041B | Temperature_HeatSink2 | I16 | 1 | ℃ |  |  | R | Radiator temperature 2 | End User
| 041C | Temperature_HeatSink3 | I16 | 1 | ℃ |  |  | R | Radiator temperature 3 | End User
| 041D | Temperature_HeatSink4 | I16 | 1 | ℃ |  |  | R | Radiator temperature 4 | End User
| 041E | Temperature_HeatSink5 | I16 | 1 | ℃ |  |  | R | Radiator temperature 5 | End User
| 041F | Temperature_HeatSink6 | I16 | 1 | ℃ |  |  | R | Radiator temperature 6 | End User
| 0420 | Temperature_Inv1 | I16 | 1 | ℃ |  |  | R | Module temperature 1 | End User
| 0421 | Temperature_Inv2 | I16 | 1 | ℃ |  |  | R | Module temperature 2 | End User
| 0422 | Temperature_Inv3 | I16 | 1 | ℃ |  |  | R | Module temperature 3 | End User
| 0423 | Temp_Rsvd1 | I16 | 1 | ℃ |  |  | R | Reserve temperature 1 | End User
| 0424 | Temp_Rsvd2 | I16 | 1 | ℃ |  |  | R | Reserve temperature 2 | End User
| 0425 | Temp_Rsvd3 | I16 | 1 | ℃ |  |  | R | Reserve temperature 3 | End User
| 0426 | GenerationTime_Today | U16 | 1 | Minute |  |  | R | Day of power generation time | End User
| 0427 | GenerationTime_Total | U32 | 1 | Minute |  |  | R | Total power generation time | End User
0428
| 0429 | ServiceTime_Total | U32 | 1 | Minute |  |  | R | Total running time | End User
042A
| 042B | InsulationResistance | U16 | 1 | kΩ |  |  | R | Insulation resistance | End User
| 042C | SysTime_Year | U16 |  |  |  |  | R | System time-year | End User
| 042D | SysTime_Month | U16 |  |  |  |  | R | System time-month | End User
| 042E | SysTime_Date | U16 |  |  |  |  | R | System Time-Daily Minutes | End User
| 042F | SysTime_Hour | U16 |  |  |  |  | R | System time-hour | End User
| 0430 | SysTime_Minute | U16 |  |  |  |  | R | System time-minutes | End User
| 0431 | SysTime_Second | U16 |  |  |  |  | R | System time-second | End User
| 0432 | Fault19 | U16 |  |  |  |  | R | Fault message table 19 | End User
| 0433 | Fault20 | U16 |  |  |  |  | R | Fault information table 20 | End User
| 0434 | Fault21 | U16 |  |  |  |  | R | Fault information table 21 | End User
| 0435 | Fault22 | U16 |  |  |  |  | R | Fault information table 22 | End User
| 0436 | Fault23 | U16 |  |  |  |  | R | Fault information table 23 | End User
| 0437 | Fault24 | U16 |  |  |  |  | R | Fault message table 24 | End User
| 0438 | Fault25 | U16 |  |  |  |  | R | Fault information table 25 | End User
| 0439 | Fault26 | U16 |  |  |  |  | R | Fault message table 26 | End User
| 043A | Fault27 | U16 |  |  |  |  | R | Fault information table 27 | End User
043B
043C
043D
043E
043F
| 0440 | AddressMask_Realtime_SysInfo2 | U64 |  |  |  |  | R | Each Character corresponds to the validity of 64 addresses in this field, . Bit4 represents the address where the highest bit address(Plus 1) of this field located 0 means invalid; 1 means valid. | End User
| 0441 | [8 empty] | End User
| 0442 | [8 empty] | End User
| 0443 | [8 empty] | End User
| 0444 | Production_Code | U16 | [5 empty] | Reversed
| 0445 | Serial_Number0 | ASCII |  |  |  |  | R | The 1st and 2nd digits of the serial number. The High 8-bits store the 1st digit of Serial Number, The low 8-bits Store the 2nd digit of Serial number | End User
| 0446 | Serial_Number1 | ASCII |  |  |  |  | R | The 3rd and 4th digits of the serial number. The High 8-bits store the 3rd digit of Serial Number, The low 8-bits Store the 4th digit of Serial number | End User
| 0447 | Serial_Number2 | ASCII |  |  |  |  | R | The 5th and 6th digits of the serial number. The High 8-bits store the5th digit of Serial Number, The low 8-bit Store the 6th digit of Serial number | End User
| 0448 | Serial_Number3 | ASCII |  |  |  |  | R | The 7th and 8th digits of the serial number. The High 8-bits store the 7th digit of Serial Number, The low 8-bits Store the 8th digit of Serial number | End User
| 0449 | Serial_Number4 | ASCII |  |  |  |  | R | The 9th and 10th digits of the serial number. The High 8-bits store the 9th digit of Serial Number, The low 8-bits Store the 10th digit of Serial number | End User
| 044A | Serial_Number5 | ASCII |  |  |  |  | R | The 11th and 12th digits of the serial number. The High 8-bits store the 11th digit of Serial Number, The low 8-bits Store the 12th digit of Serial number | End User
| 044B | Serial_Number6 | ASCII |  |  |  |  | R | The 13th and 14th digits of the serial number. The High 8-bits store the 13th digit of Serial Number, The low 8-bits Store the 14th digit of Serial number | End User
| 044C | Serial_Number7 | ASCII |  |  |  |  | R | The 15th and 16th digits of the serial number. The High 8-bits store the 15th digit of Serial Number, The low 8-bits Store the 16th digit of Serial number | End User
| 044D | Hardware_Version0 | ASCII |  |  |  |  | R | The 1st and 2nd digits of the Hardware Version. The High 8-bits store the 1st digit of Serial Number, The low 8-bits Store the 2nd digit of Serial number | End User
| 044E | Hardware_Version1 | ASCII |  |  |  |  | R | The 3rd and 4th digits of the Hardware Version. The High 8-bits store the 3rd digit of Serial Number, The low 8-bits Store the 4th digit of Serial number | End User
| 044F | Software_Version_Stage_COM | ASCII |  |  |  |  | R | Bits for communication chip's software version number. The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'. | End User
| 0450 | Software_Version_Major_COM | ASCII |  |  |  |  | R | Software version number for Communication chip. For one system, the software version number need to be consistent for all chips. The high 8 bits of the register store the higher digits. The low 8 bits of the register store the lower digits. | End User
| 0451 | Software_Version_Custom_COM | ASCII |  |  |  |  | R | Non-standard customization software version number for communication chip. The standard software version number should be"00",For one system, the Non-standard customization software version number need to be consistent for all chips, otherwise it will consider as "Fault". The high 8 bits of the register store the higher digits. The low 8 bits of the register store the lower digits. | End User
| 0452 | Software_Version_Minor_COM | ASCII |  |  |  |  | R | Subversion software number for communication chip. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 0453 | Software_Version_Stage_Master | ASCII |  |  |  |  | R | Bytes for main control chip's software version number, The lower 8 bits of the register store the ASCII code. The default value of the official version start with 'V'. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 0454 | Software_Version_Major_Master | ASCII |  |  |  |  | R | Software version number for main control chip. For one system, the software version number need to be consistent for all chips. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 0455 | Software_Version_Custom_Master | ASCII |  |  |  |  | R | Non-standard customization software version number for main control chip. The standard software version should be"00",For one system, the Non-standard customization software version number need to be consistent for all chips, otherwise it will consider as "Fault". The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 0456 | Software_Version_Minor_Master | ASCII |  |  |  |  | R | software subversion number for main control chip. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 0457 | Software_Version_Stage_Slave | ASCII |  |  |  |  | R | Bits for Secondary control chip's software version number, The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'.The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 0458 | Software_Version_Major_Slave | ASCII |  |  |  |  | R | Software version number for Secondary control chip. For one system, the software version number need to be consistent for all chips. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 0459 | Software_Version_Custom_Slave | ASCII |  |  |  |  | R | Non-standard customization software version number for secondary control chip. The standard software version should be"00",For one system, the Non-standard customization software version number need to be consistent for all chips, otherwise it will consider as "Fault". The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 045A | Software_Version_Minor_Slave | ASCII |  |  |  |  | R | software subversion number for secondary control chip. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
| 045B | Safety_Version_Major | U16 |  |  |  |  | R | main version number for Safety regulation library | End User
| 045C | Safety_version_Minor | U16 |  |  |  |  | R | Sub-version number for Safety regulation library | End User
| 045D | Boot_Version_COM | U16 |  |  |  |  | R |  | End User
| 045E | Boot_Version_Master | U16 |  |  |  |  | R |  | End User
| 045F | Boot_Version_Slave | U16 |  |  |  |  | R |  | End User
| 0460 | Safety_Firmware_Version_Stage | ASCII |  |  |  |  | R | Safety certification software version number stage definition bit. The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
| 0461 | Safety_Firmware_Version_Major | ASCII |  |  |  |  | R | The major version number of the safety certification software. The major version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
| 0462 | Safety_Firmware_Version_Custom | ASCII |  |  |  |  | R | Safety certification software non-standard customized version number. The version number of the standard software is "00". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
| 0463 | Safety_Firmware_Version_Minor | ASCII |  |  |  |  | R | Safety certification software version number. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
| 0464 | Safety_Hardware_Version0 | ASCII |  |  |  |  | R | Safety certification hardware version number 1st and 2nd. The upper 8 bits of the register store the first bit of the serial number; The lower 8 bits of the register store the second bit of the serial number. | End User
| 0465 | Safety_Hardware_Version1 | ASCII |  |  |  |  | R | The 3rd and 4th digits of the hardware version number of safety certification. The upper 8 bits of the register store the third bit of the serial number; The lower 8 bits of the register store the 4th bit of the serial number. | End User
| 0466 | Afci_Ver_Firmware | ASCII |  |  |  |  | R | afci firmware version number 'V' The high 8 bits are reserved. The lower 8 bits hold the version number.
| 0467 | Afci_Ver_Sft | ASCII |  |  |  |  | R | afci software version High 8 bits hold bit 1. Low 8 bits hold bit 2.
| 0468 | Afci_Ver_Hard | ASCII |  |  |  |  | R | afci hardware version High 8 bits hold bit 1. The lower 8 bits hold bit 2.
| 0469 | Afci_Srs_Hard | ASCII |  |  |  |  | R | afci hardware serial number High 8 bits hold bit 1. Low 8 bits hold bit 2.
| 046A | Afci_Ver_Com | ASCII |  |  |  |  | R | afci communication version High 8 bits hold bit 1. Low 8 bits hold bit 2.
046B
046C
046D
046E
046F
| 0470 | Serial_Number8 | ASCII |  |  |  |  | R | The 17th and 18th digits of the serial number. The upper 8 bits of the register store the 17th bit of the serial number; The lower 8 bits of the register store the 18th bit of the serial number. | End User
| 0471 | Serial_Number9 | ASCII |  |  |  |  | R | The 19th and 20th digits of the serial number. The high 8 bits of the register store the 19th bit of the serial number; The lower 8 bits of the register store the 20th bit of the serial number. | End User
| 0472 | Serial_Number11_Rsvd0 | ASCII |  |  |  |  | R
| 0473 | Serial_Number11_Rsvd1 | ASCII |  |  |  |  | R
| 0474 | Serial_Number12_Rsvd2 | ASCII |  |  |  |  | R
| 0475 | Serial_Number13_Rsvd3 | ASCII |  |  |  |  | R
| 0476 | Serial_Number14_Rsvd4 | ASCII |  |  |  |  | R
| 0477 | State1 | U16 |  |  |  |  | R | 状态信息表1 | End User
| 0478 | State2 | U16 |  |  |  |  | R | 状态信息表2 | End User
| 0479 | State3 | U16 |  |  |  |  | R | 状态信息表3 | End User
| 047A | State4 | U16 |  |  |  |  | R | 状态信息表4 | End User
| 047B | State5 | U16 |  |  |  |  | R | 状态信息表5 | End User
| 047C | State6 | U16 |  |  |  |  | R | 状态信息表6 | End User
| 047D | State7 | U16 |  |  |  |  | R | 状态信息表7 | End User
| 047E | State8 | U16 |  |  |  |  | R | 状态信息表8 | End User
| 047F | State9 | U16 |  |  |  |  | R | 状态信息表9 | End User
On grid output (0x0480-0x04FF)
| 0480 | AddressMask_Realtime_GridOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End User
0481
0482
0483
| 0484 | Frequency_Grid | U16 | 0.01 | Hz |  |  | R | Grid frequency | End User
| 0485 | ActivePower_Output_Total | I16 | 0.01 | kW |  |  | R | Total active power. Discharge is positive, charge is negative | End User
| 0486 | ReactivePower_Output_Total | I16 | 0.01 | kW |  |  | R | Total reactive power. The inverter end is positive for leading and negative for lagging | End User
| 0487 | ApparentPower_Output_Total | I16 | 0.01 | kW |  |  | R | Total apparent power. Discharge is positive, charge is negative | End User
| 0488 | ActivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC active power. Selling electricity is positive, buying electricity is negative | End User
| 0489 | ReactivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC reactive power. The inverter end is positive for lead and negative for lag | End User
| 048A | ApparentPower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC apparent power. Selling electricity is positive, buying electricity is negative | End User
| 048B | GridOutput_Rsvd1 | [5 empty] | R | Grid-connected output reserved 1 | End User
| 048C | GridOutput_Rsvd2 | [5 empty] | R | Grid-connected output reserved 2 | End User
| 048D | Voltage_Phase_R | U16 | 0.1 | V |  |  | R | R phase grid voltage | End User
| 048E | Current_Output_R | U16 | 0.01 | A |  |  | R | R-phase inverter output current | End User
| 048F | ActivePower_Output_R | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs active power. Discharge is positive, charge is negative | End User
| 0490 | ReactivePower_Output_R | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End User
| 0491 | PowerFactor_Output_R | I16 | 0.001 | p.u. |  |  | R | R-phase power factor. The inverter end is positive for lead and negative for lag | End User
| 0492 | Current_PCC_R | U16 | 0.01 | A |  |  | R | R phase PCC current | End User
| 0493 | ActivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R-phase PCC active power | End User
| 0494 | ReactivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End User
| 0495 | PowerFactor_PCC_R | I16 | 0.001 | p.u. |  |  | R | R-phase PCC power factor. The inverter end is positive for lead and negative for lag | End User
| 0496 | R_Rsvd1 | [5 empty] | R | R phase reserved 1 | End User
| 0497 | R_Rsvd2 | [5 empty] | R | R phase reserved 2 | End User
| 0498 | Voltage_Phase_S | U16 | 0.1 | V |  |  | R | S phase grid voltage | End User
| 0499 | Current_Output_S | U16 | 0.01 | A |  |  | R | S phase inverter output current | End User
| 049A | ActivePower_Output_S | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs active power. Discharge is positive, charge is negative | End User
| 049B | ReactivePower_Output_S | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End User
| 049C | PowerFactor_Output_S | I16 | 0.001 | p.u. |  |  | R | S-phase power factor. The inverter end is positive for lead and negative for lag | End User
| 049D | Current_PCC_S | U16 | 0.01 | A |  |  | R | S phase PCC current | End User
| 049E | ActivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S-phase PCC active power. Discharge is positive, charge is negative | End User
| 049F | ReactivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End User
| 04A0 | PowerFactor_PCC_S | I16 | 0.001 | p.u. |  |  | R | S-phase PCC power factor. The inverter end is positive for lead and negative for lag | End User
| 04A1 | S_Rsvd1 | [5 empty] | R | S phase reserved 1 | End User
| 04A2 | S_Rsvd2 | [5 empty] | R | S phase reserved 2 | End User
| 04A3 | Voltage_Phase_T | U16 | 0.1 | V |  |  | R | T phase grid voltage | End User
| 04A4 | Current_Output_T | U16 | 0.01 | A |  |  | R | T-phase inverter output current | End User
| 04A5 | ActivePower_Output_T | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs active power. Discharge is positive, charge is negative | End User
| 04A6 | ReactivePower_Output_T | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End User
| 04A7 | PowerFactor_Output_T | I16 | 0.001 | p.u. |  |  | R | T-phase power factor. The inverter end is positive for lead and negative for lag | End User
| 04A8 | Current_PCC_T | U16 | 0.01 | A |  |  | R | T phase PCC current | End User
| 04A9 | ActivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T-phase PCC active power. Discharge is positive, charge is negative | End User
| 04AA | ReactivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End User
| 04AB | PowerFactor_PCC_T | I16 | 0.001 | p.u. |  |  | R | T-phase PCC power factor. The inverter end is positive for lead and negative for lag | End User
| 04AC | T_Rsvd1 | [5 empty] | R | T phase reserved 1 | End User
| 04AD | T_Rsvd2 | [5 empty] | R | T phase reserved 2 | End User
| 04AE | ActivePower_PV_Ext | U16 | 0.01 | kW |  |  | R | External power generation | End User
| 04AF | ActivePower_Load_Sys | U16 | 0.01 | kW |  |  | R | System total load power | End User
| 04B0 | Voltage_Phase_L1N | U16 | 0.1 | V |  |  | R | Grid L1 to N voltage effective value | End User
| 04B1 | Current_Output_L1N | U16 | 0.01 | A |  |  | R | L1 output current effective value | End User
| 04B2 | ActivePower_Output_L1N | I16 | 0.01 | kW |  |  | R | Active power output on L1 line | End User
i | 04B3 | Current_PCC_L1N | U16 | 0.01 | A |  |  | R | Effective value of CT current on L1 line | End User
| 04B4 | ActivePower_PCC_L1N | I16 | 0.01 | kW |  |  | R | PCC active power on L1 line | End User
| 04B5 | Voltage_Phase_L2N | U16 | 0.1 | V |  |  | R | Grid L2 to N voltage effective value | End User
| 04B6 | Current_Output_L2N | U16 | 0.01 | A |  |  | R | L2 output current effective value | End User
| 04B7 | ActivePower_Output_L2N | I16 | 0.01 | kW |  |  | R | Active power output on L2 line | End User
| 04B8 | Current_PCC_L2N | U16 | 0.01 | A |  |  | R | Effective value of CT current on L2 line | End User
| 04B9 | ActivePower_PCC_L2N | I16 | 0.01 | kW |  |  | R | Active power output on L2 line | End User
| 04BA | Voltage_Line_L1 | U16 | 0.1 | V |  |  | R | L1 line voltage: voltage between R/S phase | End User
| 04BB | Voltage_Line_L2 | U16 | 0.1 | V |  |  | R | L2 line voltage: voltage between S/T phase | End User
| 04BC | Voltage_Line_L3 | U16 | 0.1 | V |  |  | R | L3 line voltage: voltage between T/R phase | End User
| 04BD | Power_Factor | I16 | 0.001 | p.u. |  |  | R | Total power factor. Overrun is positive and lag is negative at the inverter end | End User
04BE
04BF
04C0
04C1
04C2
04C3
04C4
04C5
04C6
04C7
04C8
04C9
04CA
04CB
04CC
04CD
04CE
04CF
04D0
04D1
04D2
04D3
04D4
04D5
04D6
04D7
04D8
04D9
04DA
04DB
04DC
04DD
04DE
04DF
04E0
04E1
04E2
04E3
04E4
04E5
04E6
04E7
04E8
04E9
04EA
04EB
04EC
04ED
04EE
04EF
04F0
04F1
04F2
04F3
04F4
04F5
04F6
04F7
04F8
04F9
04FA
04FB
04FC
04FD
04FE
04FF
Off grid output (0x0500-0x057F)
| 0500 | AddressMask_Realtime_EmergencyOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid | End User
0501
0502
0503
| 0504 | ActivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load active power. | End User
| 0505 | ReactivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load consumption is positive, and feedback is negative | End User
| 0506 | ApparentPower_Load_Total | I16 | 0.01 | kW |  |  | R | Load reactive power Apparent power of the load. Load consumption is positive, and feedback is negative | End User
| 0507 | Frequency_Output | U16 | 0.01 | Hz |  |  | R | Output voltage frequency | End User
| 0508 | ESOutput_Rsvd1 | [5 empty] | R | Off-grid total output reserved 1 | End User
| 0509 | ESOutput_Rsvd2 | [5 empty] | R | Off-grid total output reserved 2 | End User
| 050A | Voltage_Output_R | U16 | 0.1 | V |  |  | R | R-phase inverter output voltage | End User
| 050B | Current_Load_R | I16 | 0.01 | A |  |  | R | R phase load current | End User
| 050C | ActivePower_Load_R | I16 | 0.01 | kW |  |  | R | R-phase load active power. Load consumption is positive, and feedback is negative. | End User
| 050D | ReactivePower_Load_R | I16 | 0.01 | kW |  |  | R | R-phase load reactive power. The inverter end is positive for lead and negative for lag | End User
| 050E | ApparentPower_Load_R | I16 | 0.01 | kVA |  |  | R | Apparent power of R-phase load. Load consumption is positive, and feedback is negative. | End User
| 050F | LoadPeakRatio_R | U16 | 0.01 | p.u. |  |  | R | R phase load peak ratio | End User
| 0510 | Voltage_Load_R | U16 | 0.1 | V |  |  | R | R corresponding emergency load voltage | End User | R corresponding emergency load voltage
| 0511 | ESR_Rsvd2 | [5 empty] | R | R phase reserved 2 | End User
| 0512 | Voltage_Output_S | U16 | 0.1 | V |  |  | R | S phase inverter output voltage | End User
| 0513 | Current_Load_S | I16 | 0.01 | A |  |  | R | S phase load current | End User
| 0514 | ActivePower_Load_S | I16 | 0.01 | kW |  |  | R | S-phase load active power. Load consumption is positive, and feedback is negative. | End User
| 0515 | ReactivePower_Load_S | I16 | 0.01 | kW |  |  | R | S-phase load reactive power. The inverter end is positive for lead and negative for lag | End User
| 0516 | ApparentPower_Load_S | I16 | 0.01 | kVA |  |  | R | Apparent power of S-phase load. Load consumption is positive, and feedback is negative. | End User
| 0517 | LoadPeakRatio_S | U16 | 0.01 | p.u. |  |  | R | S phase load peak ratio | End User
| 0518 | Voltage_Load_S | U16 | 0.1 | V |  |  | R | S corresponding emergency load voltage | End User | S corresponding emergency load voltage
| 0519 | ESS_Rsvd2 | [5 empty] | R | S phase reserved 2 | End User
| 051A | Voltage_Output_T | U16 | 0.1 | V |  |  | R | T-phase inverter output voltage | End User
| 051B | Current_Load_T | I16 | 0.01 | A |  |  | R | T phase load current | End User
| 051C | ActivePower_Load_T | I16 | 0.01 | kW |  |  | R | T-phase load active power. Load consumption is positive, and feedback is negative. | End User
| 051D | ReactivePower_Load_T | I16 | 0.01 | kW |  |  | R | T-phase load reactive power. The inverter end is positive for lead and negative for lag | End User
| 051E | ApparentPower_Load_T | I16 | 0.01 | kVA |  |  | R | Apparent power of T-phase load. Load consumption is positive, and feedback is negative. | End User
| 051F | LoadPeakRatio_T | U16 | 0.01 | p.u. |  |  | R | T-phase load peak ratio | End User
| 0520 | Voltage_Load_T | U16 | 0.1 | V |  |  | R | T corresponding emergency load voltage | End User | T corresponding emergency load voltage
| 0521 | EST_Rsvd2 | [5 empty] | R | T phase reserved 2 | End User
| 0522 | Voltage_Output_L1N | U16 | 0.1 | V |  |  | R | Inverter L1 to N voltage effective value | End User
| 0523 | Current_Load_L1N | I16 | 0.01 | A |  |  | R | L1 load current effective value | End User
| 0524 | ActivePower_Load_L1N | I16 | 0.01 | kW |  |  | R | Load L1 to N active power | End User
| 0525 | Voltage_Output_L2N | U16 | 0.1 | V |  |  | R | Effective value of inverter L2 to N voltage | End User
| 0526 | Current_Load_L2N | I16 | 0.01 | A |  |  | R | L2 load current effective value | End User
| 0527 | ActivePower_Load_L2N | I16 | 0.01 | kW |  |  | R | Load L2 to N active power | End User
0528
0529
052A
052B
052C
052D
052E
052F
0530
0531
0532
0533
0534
0535
0536
0537
0538
0539
053A
053B
053C
053D
053E
053F
PV input (0x0580-0x05FF)
| 0580 | AddressMask_Realtime_Input_PV1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End User
0581
0582
0583
| 0584 | Voltage_PV1 | U16 | 0.1 | V |  |  | R | The first PV voltage | End User
| 0585 | Current_PV1 | U16 | 0.01 | A |  |  | R | The first PV current | End User
| 0586 | Power_PV1 | U16 | 0.01 | kW |  |  | R | PV power of the first road | End User
| 0587 | Voltage_PV2 | U16 | 0.1 | V |  |  | R | The second PV voltage | End User
| 0588 | Current_PV2 | U16 | 0.01 | A |  |  | R | The second PV current | End User
| 0589 | Power_PV2 | U16 | 0.01 | kW |  |  | R | PV power of the 2nd road | End User
| 058A | Voltage_PV3 | U16 | 0.1 | V |  |  | R | No. 3 PV voltage | End User
| 058B | Current_PV3 | U16 | 0.01 | A |  |  | R | No. 3 PV current | End User
| 058C | Power_PV3 | U16 | 0.01 | kW |  |  | R | No. 3 PV power | End User
| 058D | Voltage_PV4 | U16 | 0.1 | V |  |  | R | No. 4 PV voltage | End User
| 058E | Current_PV4 | U16 | 0.01 | A |  |  | R | No. 4 PV current | End User
| 058F | Power_PV4 | U16 | 0.01 | kW |  |  | R | No. 4 PV power | End User
| 0590 | Voltage_PV5 | U16 | 0.1 | V |  |  | R | No. 5 PV voltage | End User
| 0591 | Current_PV5 | U16 | 0.01 | A |  |  | R | No. 5 PV current | End User
| 0592 | Power_PV5 | U16 | 0.01 | kW |  |  | R | No. 5 PV power | End User
| 0593 | Voltage_PV6 | U16 | 0.1 | V |  |  | R | No. 6 PV voltage | End User
| 0594 | Current_PV6 | U16 | 0.01 | A |  |  | R | No. 6 PV current | End User
| 0595 | Power_PV6 | U16 | 0.01 | kW |  |  | R | No. 6 PV power | End User
| 0596 | Voltage_PV7 | U16 | 0.1 | V |  |  | R | No. 7 PV voltage | End User
| 0597 | Current_PV7 | U16 | 0.01 | A |  |  | R | No. 7 PV current | End User
| 0598 | Power_PV7 | U16 | 0.01 | kW |  |  | R | No. 7 PV power | End User
| 0599 | Voltage_PV8 | U16 | 0.1 | V |  |  | R | No. 8 PV voltage | End User
| 059A | Current_PV8 | U16 | 0.01 | A |  |  | R | No. 8 PV current | End User
| 059B | Power_PV8 | U16 | 0.01 | kW |  |  | R | No. 8 PV power | End User
| 059C | Voltage_PV9 | U16 | 0.1 | V |  |  | R | No. 9 PV voltage | End User
| 059D | Current_PV9 | U16 | 0.01 | A |  |  | R | No. 9 PV current | End User
| 059E | Power_PV9 | U16 | 0.01 | kW |  |  | R | No. 9 PV power | End User
| 059F | Voltage_PV10 | U16 | 0.1 | V |  |  | R | No. 10 PV voltage | End User
| 05A0 | Current_PV10 | U16 | 0.01 | A |  |  | R | No. 10 PV current | End User
| 05A1 | Power_PV10 | U16 | 0.01 | kW |  |  | R | No. 10 PV power | End User
| 05A2 | Voltage_PV11 | U16 | 0.1 | V |  |  | R | 11th PV voltage | End User
| 05A3 | Current_PV11 | U16 | 0.01 | A |  |  | R | 11th PV current | End User
| 05A4 | Power_PV11 | U16 | 0.01 | kW |  |  | R | 11th PV power | End User
| 05A5 | Voltage_PV12 | U16 | 0.1 | V |  |  | R | 12th PV voltage | End User
| 05A6 | Current_PV12 | U16 | 0.01 | A |  |  | R | 12th PV current | End User
| 05A7 | Power_PV12 | U16 | 0.01 | kW |  |  | R | 12th PV power | End User
| 05A8 | Voltage_PV13 | U16 | 0.1 | V |  |  | R | 13th PV voltage | End User
| 05A9 | Current_PV13 | U16 | 0.01 | A |  |  | R | 13th PV current | End User
| 05AA | Power_PV13 | U16 | 0.01 | kW |  |  | R | 13th PV power | End User
| 05AB | Voltage_PV14 | U16 | 0.1 | V |  |  | R | No. 14 PV voltage | End User
| 05AC | Current_PV14 | U16 | 0.01 | A |  |  | R | No. 14 PV current | End User
| 05AD | Power_PV14 | U16 | 0.01 | kW |  |  | R | No. 14 PV power | End User
| 05AE | Voltage_PV15 | U16 | 0.1 | V |  |  | R | 15th PV voltage | End User
| 05AF | Current_PV15 | U16 | 0.01 | A |  |  | R | 15th PV current | End User
| 05B0 | Power_PV15 | U16 | 0.01 | kW |  |  | R | 15th PV power | End User
| 05B1 | Voltage_PV16 | U16 | 0.1 | V |  |  | R | 16th PV voltage | End User
| 05B2 | Current_PV16 | U16 | 0.01 | A |  |  | R | 16th PV current | End User
| 05B3 | Power_PV16 | U16 | 0.01 | kW |  |  | R | 16th PV power | End User
05B4
05B5
05B6
05B7
05B8
05B9
05BA
05BB
05BC
05BD
05BE
05BF
| 05C0 | AddressMask_Realtime_Input_PV2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
05C1
05C2
05C3
| 05C4 | Power_PV_Total | U16 | 0.1 | kW |  |  | R | Total PV power | End User
05C5
05C6
05C7
05C8
05C9
05CA
05CB
05CC
05CD
05CE
05CF
05D0
05D1
05D2
05D3
05D4
05D5
05D6
05D7
05D8
05D9
05DA
05DB
05DC
05DD
05DE
05DF
05E0
05E1
05E2
05E3
05E4
05E5
05E6
05E7
05E8
05E9
05EA
05EB
05EC
05ED
05EE
05EF
05F0
05F1
05F2
05F3
Battery input (0x0600-0x067F)
| 0600 | AddressMask_Realtime_Input_Bat1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End User
0601
0602
0603
| 0604 | Voltage_Bat1 | U16 | 0.1 | V |  |  | R | No. 1 battery pack voltage | End User
| 0605 | Current_Bat1 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the first battery pack. Charge is positive, discharge is negative | End User
| 0606 | Power_Bat1 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the first battery pack. Charge is positive, discharge is negative | End User
| 0607 | Temperature_Env_Bat1 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the first battery pack | End User
| 0608 | SOC_Bat1 | U16 | 1 | % |  |  | R | No. 1 battery pack SOC | End User
| 0609 | SOH_Bat1 | U16 | 1 | % |  |  | R | No. 1 battery pack SOH | End User
| 060A | ChargeCycle_Bat1 | U16 | 1 | cycle |  |  | R | Number of cycles of the first battery pack | End User
| 060B | Voltage_Bat2 | U16 | 0.1 | V |  |  | R | No. 2 battery pack voltage | End User
| 060C | Current_Bat2 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the second battery pack. Charge is positive, discharge is negative | End User
| 060D | Power_Bat2 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the second battery pack. Charge is positive, discharge is negative | End User
| 060E | Temperature_Env_Bat2 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the second battery pack | End User
| 060F | SOC_Bat2 | U16 | 1 | % |  |  | R | 2nd battery pack SOC | End User
| 0610 | SOH_Bat2 | U16 | 1 | % |  |  | R | 2nd battery pack SOH | End User
| 0611 | ChargeCycle_Bat2 | U16 | 1 | cycle |  |  | R | Number of cycles of the second battery pack | End User
| 0612 | Voltage_Bat3 | U16 | 0.1 | V |  |  | R | No. 3 battery pack voltage | End User
| 0613 | Current_Bat3 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the third battery pack. Charge is positive, discharge is negative | End User
| 0614 | Power_Bat3 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the third battery pack. Charge is positive, discharge is negative | End User
| 0615 | Temperature_Env_Bat3 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the third battery pack | End User
| 0616 | SOC_Bat3 | U16 | 1 | % |  |  | R | No. 3 battery pack SOC | End User
| 0617 | SOH_Bat3 | U16 | 1 | % |  |  | R | No. 3 battery pack SOH | End User
| 0618 | ChargeCycle_Bat3 | U16 | 1 | cycle |  |  | R | Number of cycles of the third battery pack | End User
| 0619 | Voltage_Bat4 | U16 | 0.1 | V |  |  | R | No. 4 battery pack voltage | End User
| 061A | Current_Bat4 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 4 battery pack. Charge is positive, discharge is negative | End User
| 061B | Power_Bat4 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of the 4th battery pack. Charge is positive, discharge is negative | End User
| 061C | Temperature_Env_Bat4 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 4 | End User
| 061D | SOC_Bat4 | U16 | 1 | % |  |  | R | No. 4 battery pack SOC | End User
| 061E | SOH_Bat4 | U16 | 1 | % |  |  | R | No. 4 battery pack SOH | End User
| 061F | ChargeCycle_Bat4 | U16 | 1 | cycle |  |  | R | Number of cycles of the 4th battery pack | End User
| 0620 | Voltage_Bat5 | U16 | 0.1 | V |  |  | R | No. 5 battery pack voltage | End User
| 0621 | Current_Bat5 | I16 | 0.01 | A |  |  | R | No. 5 battery pack charging and discharging current. Charge is positive, discharge is negative | End User
| 0622 | Power_Bat5 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 5 battery pack. Charge is positive, discharge is negative | End User
| 0623 | Temperature_Env_Bat5 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 5 | End User
| 0624 | SOC_Bat5 | U16 | 1 | % |  |  | R | No. 5 battery pack SOC | End User
| 0625 | SOH_Bat5 | U16 | 1 | % |  |  | R | No. 5 battery pack SOH | End User
| 0626 | ChargeCycle_Bat5 | U16 | 1 | cycle |  |  | R | Number of cycles of the 5th battery pack | End User
| 0627 | Voltage_Bat6 | U16 | 0.1 | V |  |  | R | No. 6 battery pack voltage | End User
| 0628 | Current_Bat6 | I16 | 0.01 | A |  |  | R | No. 6 battery pack charge and discharge current. Charge is positive, discharge is negative | End User
| 0629 | Power_Bat6 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 6 battery pack. Charge is positive, discharge is negative | End User
| 062A | Temperature_Env_Bat6 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 6th battery pack | End User
| 062B | SOC_Bat6 | U16 | 1 | % |  |  | R | 6th battery pack SOC | End User
| 062C | SOH_Bat6 | U16 | 1 | % |  |  | R | No. 6 battery pack SOH | End User
| 062D | ChargeCycle_Bat6 | U16 | 1 | cycle |  |  | R | Number of cycles of the 6th battery pack | End User
| 062E | Voltage_Bat7 | U16 | 0.1 | V |  |  | R | No. 7 battery pack voltage | End User
| 062F | Current_Bat7 | I16 | 0.01 | A |  |  | R | No. 7 battery pack charging and discharging current. Charge is positive, discharge is negative | End User
| 0630 | Power_Bat7 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 7 battery pack. Charge is positive, discharge is negative | End User
| 0631 | Temperature_Env_Bat7 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 7 | End User
| 0632 | SOC_Bat7 | U16 | 1 | % |  |  | R | No. 7 battery pack SOC | End User
| 0633 | SOH_Bat7 | U16 | 1 | % |  |  | R | No. 7 battery pack SOH | End User
| 0634 | ChargeCycle_Bat7 | U16 | 1 | cycle |  |  | R | No. 7 battery pack cycle times | End User
| 0635 | Voltage_Bat8 | U16 | 0.1 | V |  |  | R | No. 8 battery pack voltage | End User
| 0636 | Current_Bat8 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 8 battery pack. Charge is positive, discharge is negative | End User
| 0637 | Power_Bat8 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 8 battery pack. Charge is positive, discharge is negative | End User
| 0638 | Temperature_Env_Bat8 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 8th battery pack | End User
| 0639 | SOC_Bat8 | U16 | 1 | % |  |  | R | No. 8 battery pack SOC | End User
| 063A | SOH_Bat8 | U16 | 1 | % |  |  | R | No. 8 battery pack SOH | End User
| 063B | ChargeCycle_Bat8 | U16 | 1 | cycle |  |  | R | Number of cycles of the 8th battery pack | End User
063C
063D
063E
063F
| 0640 | AddressMask_Realtime_Input_Bat2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End User
0641
0642
0643
| 0644 | Voltage_Bat9 | U16 | 0.1 | V |  |  | R | No. 9 battery pack voltage | End User
| 0645 | Current_Bat9 | I16 | 0.01 | A |  |  | R | No. 9 battery pack charging and discharging current. Charge is positive, discharge is negative | End User
| 0646 | Power_Bat9 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the 9th battery pack. Charge is positive, discharge is negative | End User
| 0647 | Temperature_Env_Bat9 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 9th battery pack | End User
| 0648 | SOC_Bat9 | U16 | 1 | % |  |  | R | No. 9 battery pack SOC | End User
| 0649 | SOH_Bat9 | U16 | 1 | % |  |  | R | No. 9 battery pack SOH | End User
| 064A | ChargeCycle_Bat9 | U16 | 1 | cycle |  |  | R | Number of cycles of the 9th battery pack | End User
| 064B | Voltage_Bat10 | U16 | 0.1 | V |  |  | R | No. 10 battery pack voltage | End User
| 064C | Current_Bat10 | I16 | 0.01 | A |  |  | R | No. 10 battery pack charge and discharge current. Charge is positive, discharge is negative | End User
| 064D | Power_Bat10 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 10 battery pack. Charge is positive, discharge is negative | End User
| 064E | Temperature_Env_Bat10 | I16 | 1 | ℃ |  |  | R | Ambient temperature of No. 10 battery pack | End User
| 064F | SOC_Bat10 | U16 | 1 | % |  |  | R | No. 10 battery pack SOC | End User
| 0650 | SOH_Bat10 | U16 | 1 | % |  |  | R | No. 10 battery pack SOH | End User
| 0651 | ChargeCycle_Bat10 | U16 | 1 | cycle |  |  | R | Number of cycles of the 10th battery pack | End User
| 0652 | Voltage_Bat11 | U16 | 0.1 | V |  |  | R | No. 11 battery pack voltage | End User
| 0653 | Current_Bat11 | I16 | 0.01 | A |  |  | R | The charging and discharging current of No. 11 battery pack. Charge is positive, discharge is negative | End User
| 0654 | Power_Bat11 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 11 battery pack. Charge is positive, discharge is negative | End User
| 0655 | Temperature_Env_Bat11 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 11 | End User
| 0656 | SOC_Bat11 | U16 | 1 | % |  |  | R | No. 11 battery pack SOC | End User
| 0657 | SOH_Bat11 | U16 | 1 | % |  |  | R | No. 11 battery pack SOH | End User
| 0658 | ChargeCycle_Bat11 | U16 | 1 | cycle |  |  | R | Number of cycles of the 11th battery pack | End User
| 0659 | Voltage_Bat12 | U16 | 0.1 | V |  |  | R | No. 12 battery pack voltage | End User
| 065A | Current_Bat12 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 12 battery pack. Charge is positive, discharge is negative | End User
| 065B | Power_Bat12 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 12 battery pack. Charge is positive, discharge is negative | End User
| 065C | Temperature_Env_Bat12 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 12th battery pack | End User
| 065D | SOC_Bat12 | U16 | 1 | % |  |  | R | No. 12 battery pack SOC | End User
| 065E | SOH_Bat12 | U16 | 1 | % |  |  | R | No. 12 battery pack SOH | End User
| 065F | ChargeCycle_Bat12 | U16 | 1 | cycle |  |  | R | Number of cycles of the 12th battery pack | End User
0660
0661
0662
0663
0664
0665
0666
| 0667 | Power_Bat_Total | I16 | 0.1 | kW |  |  | R | Total battery charge and discharge power. Charge is positive, discharge is negative | End User
| 0668 | SOC_Bat_Average | U16 | 1 | % |  |  | R | Summarize the average value of battery pack SOC | End User
| 0669 | SOH_Bat | U16 | 1 | % |  |  | R | Summary battery pack SOH | End User
066A
066B
066C
066D
066E
066F
0670
0671
0672
0673
0674
0675
0676
0677
0678
0679
067A
067B
067C
067D
067E
067F
Power (0x0680-0x06BF)
| 0680 | AddressMask_Realtime_ElectricityStatistics1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End User
0681
0682
0683
| 0684 | PV_Generation_Today | U32 | 0.01 | kWh |  |  | R | Power generation of the day | End User
0685
| 0686 | PV_Generation_Total | U32 | 0.1 | kWh |  |  | R | Total power generation time | End User
0687
| 0688 | Load_Consumption_Today | U32 | 0.01 | kWh |  |  | R | Load power consumption of the day | End User
0689
| 068A | Load_Consumption_Total | U32 | 0.1 | kWh |  |  | R | Total load power consumption | End User
068B
| 068C | Energy_Purchase_Today | U32 | 0.01 | kWh |  |  | R | Buy electricity on the day | End User
068D
| 068E | Energy_Purchase_Total | U32 | 0.1 | kWh |  |  | R | Total electricity purchased | End User
068F
| 0690 | Energy_Selling_Today | U32 | 0.01 | kWh |  |  | R | Electricity sold on the day | End User
0691
| 0692 | Energy_Selling_Total | U32 | 0.1 | kWh |  |  | R | Total electricity sold | End User
0693
| 0694 | Bat_Charge_Today | U32 | 0.01 | kWh |  |  | R | Battery charge capacity of the day | End User
0695
| 0696 | Bat_Charge_Total | U32 | 0.1 | kWh |  |  | R | Total battery charge | End User
0697
| 0698 | Bat_Discharge_Today | U32 | 0.01 | kWh |  |  | R | Battery discharge capacity of the day | End User
0699
| 069A | Bat_Discharge_Total | U32 | 0.1 | kWh |  |  | R | Total battery discharge | End User
069B
069C
069D
069E
069F
06A0
06A1
06A2
06A3
06A4
06A5
06A6
06A7
06A8
06A9
06AA
06AB
06AC
06AD
06AE
06AF
06B0
06B1
06B2
06B3
06B4
06B5
06B6
06B7
06B8
06B9
06BA
06BB
06BC
06BD
06BE
06BF
Internal info (0x06C0-0x06FF)
| 06C0 | AddressMask_Realtime_ClassifiedInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
06C1
06C2
06C3
| 06C4 | GFCI | U16 | 1 | mA |  |  | R | Leakage current | Installer
| 06C5 | Current_Bus_Balance | I16 | 0.01 | A |  |  | R | Balance current | Installer
| 06C6 | DCI_R | I16 | 1 | mA |  |  | R | R-phase current DC component | Installer
| 06C7 | DCI_S | I16 | 1 | mA |  |  | R | S-phase current DC component | Installer
| 06C8 | DCI_T | I16 | 1 | mA |  |  | R | T-phase current DC component | Installer
| 06C9 | DCV_R | I16 | 1 | mV |  |  | R | R-phase voltage DC component | Installer
| 06CA | DCV_S | I16 | 1 | mV |  |  | R | S-phase voltage DC component | Installer
| 06CB | DCV_T | I16 | 1 | mV |  |  | R | T-phase voltage DC component | Installer
| 06CC | Voltage_Bus | U16 | 0.1 | V |  |  | R | Total BUS voltage | Installer
| 06CD | Voltage_Bus_P | U16 | 0.1 | V |  |  | R | BUS positive voltage | Installer
| 06CE | Voltage_Bus_N | U16 | 0.1 | V |  |  | R | BUS negative voltage | Installer
| 06CF | Voltage_Bus_LLC | U16 | 0.1 | V |  |  | R | LLC Bus voltage | Installer
| 06D0 | Current_BuckBoost | I16 | 0.01 | A |  |  | R | BuckBoost current | Installer
| 06D1 | Voltage_Bus_P_Half | U16 | 0.1 | V |  |  | R | BUS positive half voltage
| 06D2 | Voltage_Bus_N_Half | U16 | 0.1 | V |  |  | R | BUS negative half voltage
| 06D3 | FlyingCap_Voltage1 | U16 | 0.1 | V |  |  | R | PV1 flying capacitor voltage
| 06D4 | FlyingCap_Voltage2 | U16 | 0.1 | V |  |  | R | PV2 flying capacitor voltage
| 06D5 | FlyingCap_Voltage3 | U16 | 0.1 | V |  |  | R | PV3 flying capacitor voltage
| 06D6 | FlyingCap_Voltage4 | U16 | 0.1 | V |  |  | R | PV4 flying capacitor voltage
| 06D7 | FlyingCap_Voltage5 | U16 | 0.1 | V |  |  | R | PV5 flying capacitor voltage
| 06D8 | FlyingCap_Voltage6 | U16 | 0.1 | V |  |  | R | PV6 flying capacitor voltage
| 06D9 | FlyingCap_Voltage7 | U16 | 0.1 | V |  |  | R | PV7 flying capacitor voltage
| 06DA | FlyingCap_Voltage8 | U16 | 0.1 | V |  |  | R | PV8 flying capacitor voltage
| 06DB | FlyingCap_Voltage9 | U16 | 0.1 | V |  |  | R | PV9 flying capacitor voltage
| 06DC | FlyingCap_Voltage10 | U16 | 0.1 | V |  |  | R | PV10 flying capacitor voltage
| 06DD | FlyingCap_Voltage11 | U16 | 0.1 | V |  |  | R | PV11 flying capacitor voltage
| 06DE | FlyingCap_Voltage12 | U16 | 0.1 | V |  |  | R | PV12 flying capacitor voltage
| 06DF | FlyingCap_Voltage13 | U16 | 0.1 | V |  |  | R | PV13 flying capacitor voltage
| 06E0 | FlyingCap_Voltage14 | U16 | 0.1 | V |  |  | R | PV14 flying capacitor voltage
| 06E1 | FlyingCap_Voltage15 | U16 | 0.1 | V |  |  | R | PV15 flying capacitor voltage
| 06E2 | FlyingCap_Voltage16 | U16 | 0.1 | V |  |  | R | PV16 flying capacitor voltage
| 06E3 | Internal_Info1 | U16 | 0.1 | V |  |  | R | Internal info 1
| 06E4 | Internal_Info2 | U16 | 0.1 | V |  |  | R | Internal info 2
| 06E5 | Internal_Info3 | U16 | 0.1 | V |  |  | R | Internal info 3
| 06E6 | Internal_Info4 | U16 | 0.1 | V |  |  | R | Internal info 4
| 06E7 | Internal_Info5 | U16 | 0.1 | V |  |  | R | Internal info 5
| 06E8 | Internal_Info6 | U16 | 0.1 | V |  |  | R | Internal info 6
| 06E9 | Internal_Info7 | U16 | 0.1 | V |  |  | R | Internal info 7
| 06EA | Internal_Info8 | U16 | 0.1 | V |  |  | R | Internal info 8
| 06EB | Internal_Info9 | U16 | 0.1 | V |  |  | R | Internal info 9
| 06EC | Internal_Info10 | U16 | 0.1 | V |  |  | R | Internal info 10
06ED
06EE
06EF
06F0
06F1
06F2
06F3
06F4
06F5
06F6
06F7
06F8
06F9
06FA
06FB
06FC
06FD
06FE
06FF
Combined info (0x0700-0x077F)
| 0700 | AddressMask_Realtime_CombinerInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
0701
0702
0703
| 0704 | Voltage_Group1 | U16 | 0.1 | V |  |  | R | The first group of bus voltage
| 0705 | Current_Group1_Branch1 | U16 | 0.01 | A |  |  | R | The first group of the first string current
| 0706 | Current_Group1_Branch2 | U16 | 0.01 | A |  |  | R | The first group and the second string current
| 0707 | Voltage_Group2 | U16 | 0.1 | V |  |  | R | The second group of bus voltage
| 0708 | Current_Group2_Branch1 | U16 | 0.01 | A |  |  | R | 2nd group 1st string current
| 0709 | Current_Group2_Branch2 | U16 | 0.01 | A |  |  | R | 2nd group 2nd string current
| 070A | Voltage_Group3 | U16 | 0.1 | V |  |  | R | The third group of bus voltage
| 070B | Current_Group3_Branch1 | U16 | 0.01 | A |  |  | R | 3rd group 1st string current
| 070C | Current_Group3_Branch2 | U16 | 0.01 | A |  |  | R | 3rd group 2nd string current
| 070D | Voltage_Group4 | U16 | 0.1 | V |  |  | R | Group 4 bus voltage
| 070E | Current_Group4_Branch1 | U16 | 0.01 | A |  |  | R | 4th group 1st string current
| 070F | Current_Group4_Branch2 | U16 | 0.01 | A |  |  | R | 4th group 2nd string current
| 0710 | Voltage_Group5 | U16 | 0.1 | V |  |  | R | Group 5 bus voltage
| 0711 | Current_Group5_Branch1 | U16 | 0.01 | A |  |  | R | 5th group 1st string current
| 0712 | Current_Group5_Branch2 | U16 | 0.01 | A |  |  | R | 5th group 2nd string current
| 0713 | Voltage_Group6 | U16 | 0.1 | V |  |  | R | Group 6 bus voltage
| 0714 | Current_Group6_Branch1 | U16 | 0.01 | A |  |  | R | 6th group 1st string current
| 0715 | Current_Group6_Branch2 | U16 | 0.01 | A |  |  | R | 6th group 2nd string current
| 0716 | Voltage_Group7 | U16 | 0.1 | V |  |  | R | Group 7 bus voltage
| 0717 | Current_Group7_Branch1 | U16 | 0.01 | A |  |  | R | 7th group 1st string current
| 0718 | Current_Group7_Branch2 | U16 | 0.01 | A |  |  | R | 7th group 2nd string current
| 0719 | Voltage_Group8 | U16 | 0.1 | V |  |  | R | Group 8 bus voltage
| 071A | Current_Group8_Branch1 | U16 | 0.01 | A |  |  | R | 8th group 1st string current
| 071B | Current_Group8_Branch2 | U16 | 0.01 | A |  |  | R | 8th group 2nd string current
| 071C | Voltage_Group9 | U16 | 0.1 | V |  |  | R | Group 9 bus voltage
| 071D | Current_Group9_Branch1 | U16 | 0.01 | A |  |  | R | 9th group 1st string current
| 071E | Current_Group9_Branch2 | U16 | 0.01 | A |  |  | R | 9th group 2nd string current
| 071F | Voltage_Group10 | U16 | 0.1 | V |  |  | R | Group 10 bus voltage
| 0720 | Current_Group10_Branch1 | U16 | 0.01 | A |  |  | R | 10th group 1st string current
| 0721 | Current_Group10_Branch2 | U16 | 0.01 | A |  |  | R | 10th group 2nd string current
| 0722 | Voltage_Group11 | U16 | 0.1 | V |  |  | R | Group 11 bus voltage
| 0723 | Current_Group11_Branch1 | U16 | 0.01 | A |  |  | R | 11th group 1st string current
| 0724 | Current_Group11_Branch2 | U16 | 0.01 | A |  |  | R | 11th group 2nd string current
| 0725 | Voltage_Group12 | U16 | 0.1 | V |  |  | R | The 12th group of bus voltage
| 0726 | Current_Group12_Branch1 | U16 | 0.01 | A |  |  | R | 12th group 1st string current
| 0727 | Current_Group12_Branch2 | U16 | 0.01 | A |  |  | R | 12th group 2nd string current
| 0728 | Voltage_Group13 | U16 | 0.1 | V |  |  | R | Group 13 bus voltage
| 0729 | Current_Group13_Branch1 | U16 | 0.01 | A |  |  | R | 13th group 1st string current
| 072A | Current_Group13_Branch2 | U16 | 0.01 | A |  |  | R | 13th group 2nd string current
| 072B | Voltage_Group14 | U16 | 0.1 | V |  |  | R | Group 14 bus voltage
| 072C | Current_Group14_Branch1 | U16 | 0.01 | A |  |  | R | The 14th group and the 1st string current
| 072D | Current_Group14_Branch2 | U16 | 0.01 | A |  |  | R | The 14th group and the 2nd string current
| 072E | Voltage_Group15 | U16 | 0.1 | V |  |  | R | Group 15 bus voltage
| 072F | Current_Group15_Branch1 | U16 | 0.01 | A |  |  | R | 15th group 1st string current
| 0730 | Current_Group15_Branch2 | U16 | 0.01 | A |  |  | R | 15th group 2nd string current
| 0731 | Voltage_Group16 | U16 | 0.1 | V |  |  | R | The 16th group of bus voltage
| 0732 | Current_Group16_Branch1 | U16 | 0.01 | A |  |  | R | The 16th group of the first string current
| 0733 | Current_Group16_Branch2 | U16 | 0.01 | A |  |  | R | 16th group 2nd string current
0734
0735
0736
0737
0738
0739
073A
073B
073C
073D
073E
073F
| 0740 | AddressMask_Realtime_CombinerInfo2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
0741
0742
0743
| 0744 | Current_Group1_Branch3 | U16 | 0.01 | A |  |  | R | Group 1, 3rd string current
| 0745 | Current_Group1_Branch4 | U16 | 0.01 | A |  |  | R | Group 1, 4th string current
| 0746 | Current_Group2_Branch3 | U16 | 0.01 | A |  |  | R | Group 2, 3rd string current
| 0747 | Current_Group2_Branch4 | U16 | 0.01 | A |  |  | R | Group 2, 4th string current
| 0748 | Current_Group3_Branch3 | U16 | 0.01 | A |  |  | R | Group 3, 3rd string current
| 0749 | Current_Group3_Branch4 | U16 | 0.01 | A |  |  | R | Group 3, 4th series current
| 074A | Current_Group4_Branch3 | U16 | 0.01 | A |  |  | R | Group 4, 3rd string current
| 074B | Current_Group4_Branch4 | U16 | 0.01 | A |  |  | R | Group 4, 4th string current
| 074C | Current_Group5_Branch3 | U16 | 0.01 | A |  |  | R | Group 5, 3rd string current
| 074D | Current_Group5_Branch4 | U16 | 0.01 | A |  |  | R | Group 5, 4th string current
| 074E | Current_Group6_Branch3 | U16 | 0.01 | A |  |  | R | Group 6, 3rd string current
| 074F | Current_Group6_Branch4 | U16 | 0.01 | A |  |  | R | Group 6, 4th string current
| 0750 | Current_Group7_Branch3 | U16 | 0.01 | A |  |  | R | Group 7, 3rd string current
| 0751 | Current_Group7_Branch4 | U16 | 0.01 | A |  |  | R | Group 7, 4th string current
| 0752 | Current_Group8_Branch3 | U16 | 0.01 | A |  |  | R | Group 8, 3rd string current
| 0753 | Current_Group8_Branch4 | U16 | 0.01 | A |  |  | R | Group 8, 4th string current
| 0754 | Current_Group9_Branch3 | U16 | 0.01 | A |  |  | R | Group 9, 3rd string current
| 0755 | Current_Group9_Branch4 | U16 | 0.01 | A |  |  | R | Group 9, 4th string current
| 0756 | Current_Group10_Branch3 | U16 | 0.01 | A |  |  | R | Group 10, 3rd string current
| 0757 | Current_Group10_Branch4 | U16 | 0.01 | A |  |  | R | Group 10, 4th string current
| 0758 | Current_Group11_Branch3 | U16 | 0.01 | A |  |  | R | Group 11, 3rd string current
| 0759 | Current_Group11_Branch4 | U16 | 0.01 | A |  |  | R | Group 11, 4th string current
| 075A | Current_Group12_Branch3 | U16 | 0.01 | A |  |  | R | Group 12, 3rd string current
| 075B | Current_Group12_Branch4 | U16 | 0.01 | A |  |  | R | Group 12, 4th string current
| 075C | Current_Group13_Branch3 | U16 | 0.01 | A |  |  | R | Group 13, 3rd string current
| 075D | Current_Group13_Branch4 | U16 | 0.01 | A |  |  | R | Group 13, 4th string current
| 075E | Current_Group14_Branch3 | U16 | 0.01 | A |  |  | R | Group 14, 3rd string current
| 075F | Current_Group14_Branch4 | U16 | 0.01 | A |  |  | R | Group 14, 4th string current
| 0760 | Current_Group15_Branch3 | U16 | 0.01 | A |  |  | R | Group 15, 3rd string current
| 0761 | Current_Group15_Branch4 | U16 | 0.01 | A |  |  | R | Group 15, 4th string current
| 0762 | Current_Group16_Branch3 | U16 | 0.01 | A |  |  | R | Group 16, 3rd string current
| 0763 | Current_Group16_Branch4 | U16 | 0.01 | A |  |  | R | Group 16, 4th string current
0764
0765
0766
0767
0768
0769
076A
076B
076C
076D
076E
076F
0770
0771
0772
0773
0774
0775
0776
0777
0778
0779
077A
077B
077C
077D
077E
077F
Arcing information (0x0780-0x07BF)
| 0780 | AddressMask_Realtime_ArcInfo3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
0781
0782
0783
| 0784 | ArcStrength_MPPT_1 | I16 | 1 |  |  |  | R | MPPT 1 Monitored Real-Time Arc Strength
| 0785 | ArcStrength_MPPT_2 | I16 | 1 |  |  |  | R | MPPT 2 monitored real-time arc intensity
| 0786 | ArcStrength_MPPT_3 | I16 | 1 |  |  |  | R | MPPT 3 Monitored real-time arc intensity
| 0787 | ArcStrength_MPPT_4 | I16 | 1 |  |  |  | R | MPPT 4 Monitored real-time arc intensity
| 0788 | ArcStrength_MPPT_5 | I16 | 1 |  |  |  | R | MPPT 5 Monitored real-time arc intensity
| 0789 | ArcStrength_MPPT_6 | I16 | 1 |  |  |  | R | MPPT 6 Monitored real-time arc intensity
| 078A | ArcStrength_MPPT_7 | I16 | 1 |  |  |  | R | MPPT 7 Monitored Real-Time Arc Strength
| 078B | ArcStrength_MPPT_8 | I16 | 1 |  |  |  | R | MPPT 8 Monitored Real-Time Arc Strength
| 078C | ArcStrength_MPPT_9 | I16 | 1 |  |  |  | R | MPPT 9 Monitored Real-Time Arc Strength
| 078D | ArcStrength_MPPT_10 | I16 | 1 |  |  |  | R | MPPT 10 Monitored Real-Time Arc Strength
| 078E | ArcStrength_MPPT_11 | I16 | 1 |  |  |  | R | MPPT 11 Monitored Real-Time Arc Strength
| 078F | ArcStrength_MPPT_12 | I16 | 1 |  |  |  | R | MPPT 12 Monitored Real-Time Arc Strength
| 0790 | ArcStrength_MPPT_13 | I16 | 1 |  |  |  | R | MPPT 13 Monitored Real-Time Arc Strength
| 0791 | ArcStrength_MPPT_14 | I16 | 1 |  |  |  | R | MPPT 14 Monitored Real-Time Arc Strength
| 0792 | ArcStrength_MPPT_15 | I16 | 1 |  |  |  | R | MPPT 15 Monitored Real-Time Arc Strength
| 0793 | ArcStrength_MPPT_16 | I16 | 1 |  |  |  | R | MPPT 16 Monitored Real-Time Arc Strength
| 0794 | ArcStrength_MPPT_17 | I16 | 1 |  |  |  | R | MPPT 17 Monitored Real-Time Arc Strength
| 0795 | ArcStrength_MPPT_18 | I16 | 1 |  |  |  | R | MPPT 18 Monitored Real-Time Arc Strength
| 0796 | ArcStrength_MPPT_19 | I16 | 1 |  |  |  | R | MPPT 19 Monitored Real-Time Arc Strength
| 0797 | ArcStrength_MPPT_20 | I16 | 1 |  |  |  | R | MPPT 20 Monitored Real-Time Arc Strength
| 0798 | ArcStrength_MPPT_21 | I16 | 1 |  |  |  | R | MPPT 21 Monitored Real-Time Arc Strength
| 0799 | ArcStrength_MPPT_22 | I16 | 1 |  |  |  | R | MPPT 22 Monitored Real-Time Arc Strength
| 079A | ArcStrength_MPPT_23 | I16 | 1 |  |  |  | R | MPPT 23 Monitored Real-Time Arc Strength
| 079B | ArcStrength_MPPT_24 | I16 | 1 |  |  |  | R | MPPT 24 Monitored Real-Time Arc Intensity
079C
079D
079E
079F
07A0
07A1
| 07A2 | ArcStrength_history_Channel1 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 1 is powered on Maximum value, automatically cleared after power failure
| 07A3 | ArcStrength_history_Channel2 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 2 is powered on Maximum value, automatically cleared after power failure
| 07A4 | ArcStrength_history_Channel3 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 3 is powered on Maximum value, automatically cleared after power failure
| 07A5 | ArcStrength_history_Channel4 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 4 is powered on Maximum value, automatically cleared after power failure
| 07A6 | ArcStrength_history_Channel5 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 5 is powered on Maximum value, automatically cleared after power failure
| 07A7 | ArcStrength_history_Channel6 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 6 is powered on Maximum value, automatically cleared after power failure
| 07A8 | ArcStrength_history_Channel7 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 7 is powered on Maximum value, automatically cleared after power failure
| 07A9 | ArcStrength_history_Channel8 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 8 is powered on Maximum value, automatically cleared after power failure
| 07AA | ArcStrength_history_Channel9 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 9 is powered on Maximum value, automatically cleared after power failure
| 07AB | ArcStrength_history_Channel10 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 10 is powered on Maximum value, automatically cleared after power failure
| 07AC | ArcStrength_history_Channel11 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 11 is powered on Maximum value, automatically cleared after power failure
| 07AD | ArcStrength_history_Channel12 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 12 is powered on Maximum value, automatically cleared after power failure
| 07AE | ArcStrength_history_Channel13 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 13 is powered on Maximum value, automatically cleared after power failure
| 07AF | ArcStrength_history_Channel14 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 14 is powered on Maximum value, automatically cleared after power failure
| 07B0 | ArcStrength_history_Channel15 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 15 is powered on Maximum value, automatically cleared after power failure
| 07B1 | ArcStrength_history_Channel16 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 16 is powered on Maximum value, automatically cleared after power failure
| 07B2 | ArcStrength_history_Channel17 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 17 is powered on Maximum value, automatically cleared after power failure
| 07B3 | ArcStrength_history_Channel18 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 18 is powered on Maximum value, automatically cleared after power failure
| 07B4 | ArcStrength_history_Channel19 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 19 is powered on Maximum value, automatically cleared after power failure
| 07B5 | ArcStrength_history_Channel20 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 20 is powered on Maximum value, automatically cleared after power failure
| 07B6 | ArcStrength_history_Channel21 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 21 is powered on Maximum value, automatically cleared after power failure
| 07B7 | ArcStrength_history_Channel22 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 22 is powered on Maximum value, automatically cleared after power failure
| 07B8 | ArcStrength_history_Channel23 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 23 is powered on Maximum value, automatically cleared after power failure
| 07B9 | ArcStrength_history_Channel24 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 24 is powered on Maximum value, automatically cleared after power failure
07BA
07BB
07BC
07BD
07BE
07BF
Safety Parameter Area(0x0800-0x0FFF)
Boot Parameters (0x0800-0x083F)
| 0800 | ConnectWaitTime | U16 | 1 | Second | 1 | 65535 | RW | Waiting time before generate on grid power | Installer
| 0801 | PowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100 mean fully power sided in one minute, Other values are calculated based on this | Installer
| 0802 | ReconnectWaitTime | U16 | 1 | Second | 1 | 65535 | RW | Waiting time after grid fault recovery | Installer
| 0803 | ReconnectPowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100 mean fully power sided in one minute, Other values are calculated based on this | Installer
| 0804 | VoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | Upper limit for starting voltage (Grid side) | End User
| 0805 | VoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | Lower limit for starting Voltage (Grid Side) | End User
| 0806 | FreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Upper limit for starting frequency (Grid side) | End User
| 0807 | FreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Lower limit for starting Frequency (Grid Side) | End User
| 0808 | ReconnectVoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | Upper limit for reconnected grid voltage | End User
| 0809 | ReconnectVoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | Lower limit For reconnected grid voltage | End User
| 080A | ReconnectFreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Upper limit for reconnected grid frequency | End User
| 080B | ReconnectFreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Lower limit for reconnected grid frequency | End User
Grid voltage protection Parameters (0x0840-0x087F)
| 0840 | Voltage Config | U16 |  |  |  |  | RW | Bit0：OV1 protection enable bits Bit1：OV2 protection enable bits Bit2：OV3 protection enable bit Bit3：UV1 protection enable bits Bit4：UV2 protection enable bits Bit5：UV3 Protection enable bits Bit6：over voltage protection enable bits(ten minutes time period) | Installer
| 0841 | RatedVoltage | U16 | 0.1 | V | 0 | 65535 | RW | Grid Rated voltage | Installer
| 0842 | FirstOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | OV1 trigger Value | End User
| 0843 | FirstOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OV1 trigger time | Installer
| 0844 | SecondOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | OV2 Trigger Value | End User
| 0845 | SecondOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OV2 Trigger time | Installer
| 0846 | ThirdOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | OV3 Trigger value | End User
| 0847 | ThirdOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OV3 Trigger Time | Installer
| 0848 | FirstUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | UV1 trigger Value | End User
| 0849 | FirstUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UV1 trigger time | Installer
| 084A | SecondUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | UV2 Trigger Value | End User
| 084B | SecondUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UV2 Trigger time | Installer
| 084C | ThirdUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | UV3 Trigger value | End User
| 084D | ThirdUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UV3 Trig+K852:K863ger Time | Installer
| 084E | 10MinOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Over Voltage protection for Ten minutes range | Installer
| 084F | FirstOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | First level overvoltage protection time high | Installer
| 0850 | SecondOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | Second level overvoltage protection time high | Installer
| 0851 | ThirdOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | Third level overvoltage protection time high | Installer
Frquency Protection Parameter (0x0880-0x08BF)
| 0880 | FrequencyConfig | U16 |  |  |  |  | RW | Bit0：OF1 protection enable bits Bit1：OF2 protection enable bits Bit2：OF3 protection enable bit Bit3：UF1 protection enable bits Bit4：UF2 protection enable bits Bit5：UF3 Protection enable bits | Installer
| 0881 | RatedFrequency | U16 | 0.01 | Hz | 4000 | 7000 | RW | Grid Rated Frequency | Installer
| 0882 | FirstOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | OF1 Trigger Value | End User
| 0883 | FirstOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OF1 trigger time | Installer
| 0884 | SecondOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | OF2 Trigger Value | End User
| 0885 | SecondOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OF2 Trigger time | Installer
| 0886 | ThirdOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | OF3 Trigger value | End User
| 0887 | ThirdOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OF3 Trigger Time | Installer
| 0888 | FirstUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | UF1 trigger Value | End User
| 0889 | FirstUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UF1 trigger time | Installer
| 088A | SecondUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | UF2 Trigger Value | End User
| 088B | SecondUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UF2 Trigger time | Installer
| 088C | ThirdUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | UF3 Trigger value | End User
| 088D | ThirdUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UF3 Trigger Time | Installer
DCIProtection Parameter (0x08C0-0x08FF)
| 08C0 | DCI Config | U16 |  |  |  |  | RW | Bit0：DCI level 1 protection Bit1：DCI level 2 protection Bit2：DCI level 3 protection Bit3：DCI testing enable bot | Installer
| 08C1 | DCIFirstProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI level 1 tripping value | Installer
| 08C2 | DCIFirstProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI level 1 tripping time | Installer
| 08C3 | DCISecondProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI level 2 tripping value | Installer
| 08C4 | DCISecondProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI level 2 tripping tie | Installer
| 08C5 | DCIThirdProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI level 3 tripping value | Installer
| 08C6 | DCIThirdProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI level 3 tripping time | Installer
| 08C7 | DCITestValue1 | I16 | 1 | mA | -32768 | 32767 | RW | DCI phase R testing value | Installer
| 08C8 | DCITestValue2 | I16 | 1 | mA | -32768 | 32767 | RW | DCI phase S testing value | Installer
| 08C9 | DCITestValue3 | I16 | 1 | mA | -32768 | 32767 | RW | DCI phase T testing value | Installer
| 08CA | DCIFirstProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI level 1 protection Ratio | Installer
| 08CB | DCISecondProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI level 2 protection Ratio | Installer
| 08CC | DCIThirdProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI level 3 protection Ratio | Installer
Active power &Over/Under voltage Power Derate Paramter (0x0900-0x093F)
| 0900 | Remote Config | U16 |  |  |  |  | RW | Bit0：Active power derate Bit1：remtely on/off control Bit2：power derate leading by high AC voltage Bit3：battery charging power derate leading high voltage Bit4：battery charging power derate by low voltage Bit5：DRM0 Bit6：logic interface（DRM1-8） Bit7: Anti-backflow overload enable bit Bit8: Voltage dropout PT curve enable bit | Installer
| 0901 | ActiveOutputLimit | U16 | 0.1 | % | 0 | 1000 | RW | The percentage of active power output | Installer
| 0902 | ActiveOutputDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | active power derating rate | Installer
| 0903 | GridVoltageDropStart | U16 | 0.1 | V | 0 | 65535 | RW | the start point of power derate leading by high grid voltage | Installer
| 0904 | GridVoltageDropStop | U16 | 0.1 | V | 0 | 65535 | RW | the end point of power derate leading by high ac voltage | Installer
| 0905 | GridVoltageDropMinPower | I16 | 1 | % | -100 | 100 | RW | cut -off power of power derate leading by high ac voltage | Installer
| 0906 | OvervoltageDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | power derating rate leading by high ac voltage | Installer
| 0907 | ChgDerateVoltStart | U16 | 0.1 | V | 0 | 65535 | RW | the start point of power derate leading by low grid voltage | Installer
| 0908 | ChgDerateVoltEnd | U16 | 0.1 | V | 0 | 65535 | RW | the end point of power derate leading by low ac voltage | Installer
| 0909 | ChgDerateMinPower | I16 | 1 | % | -100 | 100 | RW | cut -off power of power derate leading by low ac voltage | Installer
| 090A | PowerForLogic1 | I16 | 1 | % | -100 | 100 | RW | logic interface 1 corresponding power | Installer
| 090B | PowerForLogic2 | I16 | 1 | % | -100 | 100 | RW | logic interface 2 corresponding power | Installer
| 090C | PowerForLogic3 | I16 | 1 | % | -100 | 100 | RW | logic interface 3 corresponding power | Installer
| 090D | PowerForLogic4 | I16 | 1 | % | -100 | 100 | RW | logic interface 4 corresponding power | Installer
| 090E | PowerForLogic5 | I16 | 1 | % | -100 | 100 | RW | logic interface 5 corresponding power | Installer
| 090F | PowerForLogic6 | I16 | 1 | % | -100 | 100 | RW | logic interface 6 corresponding power | Installer
| 0910 | PowerForLogic7 | I16 | 1 | % | -100 | 100 | RW | logic interface 7 corresponding power | Installer
| 0911 | PowerForLogic8 | I16 | 1 | % | -100 | 100 | RW | logic interface 8 corresponding power | Installer
| 0912 | RefluxPower | U16 | 1 | % | 0 | 100 | RW | Reflux power (upper limit of VDE4105 safety grid-connected power) | Installer
| 0913 | RefluxOVloadTime | U16 | 10 | ms | 0 | 65535 | RW | Reflux power over load (upper limit of VDE4105 safety grid-connected power) | Installer
| 0914 | LogicDerateSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | Logical interface derating rate | Installer
| 0915 | LogicReloadSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | Logical interface reload rate | Installer
| 0916 | VoltageDerateResponseTime | U16 | 1 | Second | 0 | 65535 | RW | Voltage derate time | Installer
Over/Under Frquency Power Derate (0x0940-0x097F)
| 0940 | FrequencyDerateConfig | U16 |  |  |  |  | RW | Bit0：enable, higher frequency power derate Bit1：enable, lower frequency power derate Bit2：enable, higher frequency power reload Bit3：enable, lower frequency power reload Bit4：enable,power derate start from rated power Bit5：enable,derating slope calculate by current power Bit6: Energy storage segmentation curve enable Bit7: Maximum power calculation enable Bit12-13：derating mode(0: slope mode ; 1:frquency mode) | Installer
| 0941 | OverfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | the Starting point of power derate leading by higher frequency | Installer
| 0942 | OverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | The ending point of power derate leading by higher frequency | Installer
| 0943 | OverfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | the percentage of power derate leading higher frequency German Standard slope=1/(s*fn) | Installer
| 0944 | OverfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power derate leading by higher frequency | Installer
| 0945 | OverfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power reload leading by higher frequency | Installer
| 0946 | OverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | reload frequency for power reload leading by higher frequency | Installer
| 0947 | OverfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | the percentage of power reload rate leading by higher frequency | Installer
| 0948 | UnderfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | the Starting point of power derate leading by lower frequency | Installer
| 0949 | UnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | The ending point of power derate leading by lower frequency | Installer
| 094A | UnderfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | the percentage of power derate leading lower frequency German Standard slope=1/(s*fn) | Installer
| 094B | UnderfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power derate leading by lower frequency | Installer
| 094C | UnderfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power reload leading by lower frequency | Installer
| 094D | UnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | reload frequency for power reload leading by lower frequency | Installer
| 094E | UnderfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | the percentage of power reload rate leading by lower frequency | Installer
| 094F | FrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | Highest frequency to exist load reduction. | Installer
| 0950 | FrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | lowest frequency to exist load reduction. | Installer
| 0951 | ESSOverFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency derate start frequency | Installer
| 0952 | ESSOverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) cut-off frequency for over-frequency derate. Frequency range mode is valid | Installer
| 0953 | ESSOverFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy storage) Over-frequency derate slope percentage. Slope mode is valid German standard slope=1/(s*fn) | Installer
| 0954 | ESSOverFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Over-frequency derate start-up waiting time | Installer
| 0955 | ESSOverFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Waiting time before over-frequency reload | Installer
| 0956 | ESSOverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency derate reloading frequency. It takes effect when over-frequency reload is prohibited. | Installer
| 0957 | ESSOverFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | (Energy storage) Over-frequency reload rate percentage | Installer
| 0958 | ESSUnderFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency derate start frequency | Installer
| 0959 | ESSUnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) cut-off frequency of under-frequency derate. Frequency range mode is valid | Installer
| 095A | ESSUnderFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy storage) Under-frequency derate slope percentage. Slope mode is valid | Installer
| 095B | ESSUnderFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Under-frequency derate start-up waiting time | Installer
| 095C | ESSUnderFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) waiting time before under-frequency reload | Installer
| 095D | ESSUnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency derate reloading frequency. It takes effect when Under-frequency reload is prohibited. | Installer
| 095E | ESSUnderFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | (Energy storage) Percentage of under-frequency reload rate | Installer
| 095F | ESSFrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) The highest frequency for exiting derate. Over&Under-frequency sharing | Installer
| 0960 | ESSFrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) The lowest frequency for exiting derate. Over&Under-frequency sharing | Installer
| 0961 | ESSOverFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency derate power crosses the frequency point. It is valid when 0940 Bit6 is enabled. | Installer
| 0962 | ESSUnderFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency derate power crosses the frequency point. It is valid when 0940 Bit6 is enabled. | Installer
Reactive power Parameter (0x0980-0x09BF)
| 0980 | ReactiveConfig | U16 |  |  |  |  | RW | Bit0：enable reactive power Bit1-3：reactive power mode Bit8：enable, reactive mode 3 (voltage mode ) Bit9: Charge reactive enable Bit10: Reactive mode four Austrian enable bit | Installer
| 0981 | PowerFactor | I16 | 0.0001 |  | -10000 | 10000 | RW | power factor, by using reactive mode 1 to calculate Tanphi | Installer
| 0982 | FixedReactivePercentage | I16 | 0.01 | % | -6000 | 6000 | RW | fixed percentage pf reactive power, calculate the reactive power by using reactive mode 2 | Installer
| 0983 | ReactiveCos1 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 1st point power factor | Installer
| 0984 | ReactivedynamicValue1 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 1st point power percentage | Installer
| 0985 | ReactiveCos2 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 2nd point power factor | Installer
| 0986 | ReactivedynamicValue2 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 2nd point power percentage | Installer
| 0987 | ReactiveCos3 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 3rd point power factor | Installer
| 0988 | ReactivedynamicValue3 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 3rd point power percentage | Installer
| 0989 | ReactiveCos4 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 4th point power factor | Installer
| 098A | ReactivedynamicValue4 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 4th point power percentage | Installer
| 098B | LockinV | U16 | 1 | % | 0 | 200 | RW | For reactive mode 3，the lochinV voltage percentage | Installer
| 098C | LockoutV | U16 | 1 | % | 0 | 200 | RW | For reactive mode 3，the lochoutV voltage percentage | Installer
| 098D | HighVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 4, the percentage of higher voltage start up point | Installer
| 098E | HighVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | For Reactive mode 4, the percentage of higher voltage ending point | Installer
| 098F | LowVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | for reactive mode 4 ,the percentage of lower voltage start up point | Installer
| 0990 | LowVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 4, the percentage of lower voltage ending point | Installer
| 0991 | LockinPower4 | U16 | 1 | % | 0 | 100 | RW | For reactive mode 4 ，Lockinpower percentage | Installer
| 0992 | LockoutPower4 | U16 | 1 | % | 0 | 100 | RW | For Reactive mode 4，Lockout power percentage | Installer
| 0993 | MaxLeadingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | for Reactive mode 4 , The max reactive power percentage | Installer
| 0994 | ReactiveResponseWaitTime4 | U16 | 10 | ms | 0 | 65535 | RW | For Reactive mode 4, waiting time for reactive power response | Installer
| 0995 | ReactivePowerOffset4 | I16 | 0.01 | %Qmax | -10000 | 10000 | RW | For Reactive mode4, reactive power offset value | Installer
| 0996 | ReactivePowerStart4 | U16 | 0.01 | %Pn | -10000 | 10000 | RW | For reactive mode 4, the percentage of reactive power (higher voltage start point) | Installer
| 0997 | HighVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 5, the percentage of higher voltage start up point | Installer
| 0998 | HighVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | For Reactive mode 5, the percentage of higher voltage ending point | Installer
| 0999 | LowVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | for reactive mode 5 ,the percentage of lower voltage start up point | Installer
| 099A | LowVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 5, the percentage of lower voltage ending point | Installer
| 099B | LockinPower5 | U16 | 1 | % | 0 | 100 | RW | For reactive mode 5 ，Lockinpower percentage | Installer
| 099C | LockoutPower5 | U16 | 1 | % | 0 | 100 | RW | For Reactive mode 5，Lockout power percentage | Installer
| 099D | MaxReactivePower5 | U16 | 0.01 | % | 0 | 10000 | RW | for Reactive mode 5 , The max reactive power percentage | Installer
| 099E | ReactiveResponseWaitTime5 | U16 | 10 | ms | 0 | 65535 | RW | For Reactive mode 5, waiting time for reactive power response | Installer
| 099F | PhaseType | U16 |  |  | 0 | 2 | RW | For Reactive mode 6 ，phase type 0：no Reactive power 1：lagging 2：leading | Installer
| 09A0 | ReactiveResponsePeriod | U16 | 1 | Second | 1 | 65535 | RW | for reactive mode （1, 2, 3, 4, 5, 6）adjust the time period for reactive power mode | Installer
| 09A1 | MaxLaggingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | Reactive power mode four, the maximum lagging reactive power percentage | Installer
09A2
09A3
09A4
09A5
09A6
09A7
09A8
09A9
Voltage ride through Parameter (0x09C0-0x09FF)
| 09C0 | VRTConfig | U16 |  |  |  |  | RW | Bit0：LVRT enable bit Bit1：OVRT enable bit Bit2：0 current mode enable bot BIt3：Keep reactive current before VRT Bit4: Calculate the current using the voltage before the drop Bit5: Negative sequence current enable bit Bit6: High through active enable bit Bit8-11：VRT current calculation Mode | Installer
| 09C1 | LvrtInVolt | U16 | 1 | % | 0 | 65535 | RW | The Voltage percentage (start point,LVRT) | Installer
| 09C2 | LvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (1st point, LVRT) | Installer
| 09C3 | LvrtFirstPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 1st point ,LVRT | Installer
| 09C4 | LvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (2ND point, LVRT) | Installer
| 09C5 | LvrtSecondPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 2nd point ,LVRT | Installer
| 09C6 | LvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (3rd point, LVRT) | Installer
| 09C7 | LvrtThirdPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 3rd point ,LVRT | Installer
| 09C8 | LvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (4th point, LVRT) | Installer
| 09C9 | LvrtFourthPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 4th point ,LVRT | Installer
| 09CA | LvrtReactiveCurrentCoefficientK | U16 | 0.1 | p.u. | 0 | 65535 | RW | Reactive Current Coefficient (K），LVRT | Installer
| 09CB | LvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after LVRT Recovery | Installer
| 09CC | LvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | Power reload rate (back from LVRT) | Installer
| 09CD | OvrtInVlot | U16 | 1 | % | 0 | 65535 | RW | The Voltage percentage (start point,OVRT) | Installer
| 09CE | OvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (1st point, OVRT) | Installer
| 09CF | OvrtFirstPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 1st point ,OVRT | Installer
| 09D0 | OvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (2ND point, OVRT) | Installer
| 09D1 | OvrtSecondPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 2nd point ,OVRT | Installer
| 09D2 | OvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (3rd point, OVRT) | Installer
| 09D3 | OvrtThirdPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 3rd point ,OVRT | Installer
| 09D4 | OvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (4th point, OVRT) | Installer
| 09D5 | OvrtFourthPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 4th point ,OVRT | Installer
| 09D6 | OvrtReactiveCurrentCoefficientK | U16 | 0.1 | p.u. | 0 | 65535 | RW | Reactive Current Coefficient (K），OVRT | Installer
| 09D7 | OvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after OVRT Recovery | Installer
| 09D8 | OvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | Power reload rate (back from OVRT) | Installer
| 09D9 | ZeroCurrentModeInLowVolt | U16 | 1 | % | 0 | 65535 | RW | the percentage to low voltage mode from zero current mode | Installer
| 09DA | ZeroCurrentModeInHighVolt | U16 | 1 | % | 0 | 65535 | RW | the percentage to high voltage mode from zero current mode | Installer
| 09DB | LvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage for LVRT EXIST | Installer
| 09DC | LvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | The starting point, voltage percentage for reactive current calculation(LVRT) | Installer
| 09DD | OvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage for OVRT EXIST | Installer
| 09DE | OvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | The starting point, voltage percentage for reactive current calculation(0VRT) | Installer
| 09DF | MaxIqPct | U16 | 1 | % | 0 | 65535 | RW | Maximum reactive current percentage | Installer
islanding、GFCI、ISO Parameter (0x0A00-0x0A3F)
| 0A00 | IslandConfig | U16 |  |  |  |  | RW | Bit0：ISLANDING ENABLE BIT | Installer
| 0A01 | GFCIConfig | U16 |  |  |  |  | RW | Bit0：GFCI enable bit | Installer
| 0A02 | ISOConfig | U16 |  |  |  |  | RW | Bit0：Insulation Resistance testing enable bit Bit1：ground Testing enable bit | Installer
| 0A03 | InsulationProtectionValue | U16 | 1 | kΩ | 30 | 65535 | RW | Insulation resistance Value | Installer
| 0A04 | IsoLeakageCurrentLimit | U16 | 1 | mA | 1 | 50 | RW | leakage current limit , PV to ground | Installer
| 0A05 | GFCILimit | U16 | 1 | mA/kVA | 1 | 50 | RW | Leakage current limit（not to public , can not make change） | Installer
| 0A06 | PE_N_Config | U16 |  |  |  |  | RW | PE and N control register Bit0: Off-net PEN short enable bit Bit1: N line detection enable bit | Installer
| 0A07 | IslandDetectSensitivity | U16 |  |  |  |  | RW | Sensitivity of islanding detection | Installer
| 0A08 | PEProtectionValue | U16 | 1 | kΩ | 1000 | 65535 | RW | Ground fault judgment threshold | Installer
0A09
0A0A
0A0B
0A0C
0A0D
ARC (0x0A40-0x0A7F)
| 0A40 | [8 empty] | Installer
Paramters setting (0x1000-0x17FF)
Basic Parameter Configuration (0x1000-0x10FF)
| 1000 | AddressMask_Config_Basic1 | U64 |  |  |  |  | R | Each Character in this field, will verify the validity of 64 addresses. Bit4 represents the address where the highest bit address of this field plus 1, 0 means invalid; 1 means valid. | End User
| 1001 | [8 empty] | End User
| 1002 | [8 empty] | End User
| 1003 | [8 empty] | End User
| 1004 | SysTimeConfig_Year | U16 |  | Year | 0 | 99 | RW | System time -year,Actual year=2000+values in Register | End User
| 1005 | SysTimeConfig_Month | U16 |  | Month | 1 | 12 | RW | System time-Month | End User
| 1006 | SysTimeConfig_Date | U16 |  | date | 1 | 31 | RW | System time-Date | End User
| 1007 | SysTimeConfig_Hour | U16 |  | Hour | 0 | 23 | RW | System time -Hour | End User
| 1008 | SysTimeConfig_Minute | U16 |  | Minute | 0 | 59 | RW | System Time -Minutes | End User
| 1009 | SysTimeConfig_Second | U16 |  | Second | 0 | 59 | RW | System Time-Second | End User
| 100A | SysTimeConfig_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
| 100B | RS485Config_Address | U16 |  |  | 1 | 247 | RW | RS 485 configuration- communication address | End User
| 100C | RS485Config_Baud | U16 |  |  | 0 | 4 | RW | RS485 Baud Rate Selection 0：4800bps 1：9600bps（Default） 2：19200bps 3：38400bps 4：57600bps 5：115200bps 10：1200bps 11：2400bps | End User
| 100D | RS485Config_StopBit | U16 |  |  | 0 | 2 | RW | RS485Stop bit selection； 0：1bit stop bit（Default） 1：1.5 bit stop bit 2：2bit stop bit | End User
| 100E | RS485Config_ParityBit | U16 |  |  | 0 | 4 | RW | RS485 check bit selection； 0：No Check/None（Default） 1：Even 2：Odd 3：HIgh/Mark 4：Low/Space | End User
| 100F | RS485Config_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
| 1010 | PV_InputMode_Config | U16 |  |  | 0 | 1 | RW | PV input Mode Selection 0: Parallel Mode 1:Independent mode | End User
| 1011 | InputType_Channel0_Config | U16 |  |  | 0 | 255 | RW | 0 Type input channel Selection Value "0" mean current input power supply are not available Vale Between "1～127" mean current input power supply by PV； Value between "128~255" mean input power supply by battery； If we got two or more than two values , and all values bogger than 0, it mean input power supply by PV & Battery | End User
| 1012 | InputType_Channel1_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1013 | InputType_Channel2_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1014 | InputType_Channel3_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1015 | InputType_Channel4_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1016 | InputType_Channel5_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1017 | InputType_Channel6_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1018 | InputType_Channel7_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1019 | InputType_Channel8_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 101A | InputType_Channel9_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 101B | InputType_Channel10_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 101C | InputType_Channel11_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 101D | InputType_Channel12_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 101E | InputType_Channel13_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 101F | InputType_Channel14_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1020 | InputType_Channel15_Config | U16 |  |  | 0 | 255 | RW |  | Installer
| 1021 | InputType_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
| 1022 | SafetyUpdateFromUSB_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
| 1023 | AntiReflux_Control | U16 |  |  | 0 | 2 | RW | Reflux Power control input value 0, disable the reflux power input value 1, power reflux enable with minimum power among the three phase input value 2, power reflux enable with meaning value | Installer
| 1024 | AntiReflux_Power | U16 | 100 | W | 0 | 65535 | RW | Reflux power | Installer
| 1025 | IVCurveScan_Control | U16 |  |  | 0 | 1 | RW | IV curve scan control | Installer
| 1026 | IVCurveScan_Period | U16 | 1 | Minute | 5 | 65535 | RW | Iv Curve scan cycle | Installer
| 1027 | IVCurveScan_Oneshot | U16 |  |  | 1 | 1 | RW | IV curve scan enable, input value 1, enable the I-V curve one time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
| 1028 | IVCurveScan_ReadChannel | U16 |  |  | 0 | 31 | RW | Channel for IV curve scan return value. This register used to specify the PV channel corresponding to the return value of the IV curve scan result. | Installer
| 1029 | EPS_Control | U16 |  |  | 0 | 2 | RW | Emergency Power supply 1: disable emergency power supply 2 enable emergency power supply ,disable cold start 3enable emergency power supply enable cold start | End User
| 102A | EPS_WaitTime | U16 | 1 | Second | 0 | 65535 | RW | Waiting time for emergency power start (Reverse Function) | End User
| 102B | BatteryActive_Control | U16 |  |  | 0 | 1 | RW | Battery automatic activation | End User
| 102C | BatteryActive_Oneshot | U16 |  |  | 1 | 1 | RW | Battery active input value 1, enable the battery active one time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
| 102D | CT_Auto_Calibrate | U16 |  |  | 1 | 1 | RW | CT Calibration(Automatic) input value 1, enable the CT calibration one time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
| 102E | Italy_AutoTest | U16 |  |  | 1 | 2 | RW | Italy automatic test Write: Operate standard test; 0x0002: Operate quick test; When reading, return the status of the last write operation: 0x0000: success 0x0001: Standard test is being operated 0x0002: Quick test is being operated 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, and the input parameters are incorrect | Installer
| 102F |  | U16 |  |  |  |  | RW |  | Installer
| 1030 | EnergyStatistics_Date_Year | U16 | 1 | Year | 0 | 19 | RW | Register for statistics power return date. This register indicate specifics year of the returned energy data. Year refers to the Nth most recent year relative to the inverter system time. N is the register value. 0: the current year of the system time; 1: 1 year before the system time; 19：19 year before the system time | Installer
| 1031 | EnergyStatistics_Date_Month | U16 | 1 | Month | 1 | 12 | RW | Register for statistics power return date. This register indicate specifics month of the returned energy data | Installer
| 1032 | EnergyStatistics_Date_Date | U16 | 1 | date | 1 | 31 | RW | Register for statistics power return date. This register indicate specifics Day of the returned energy data | Installer
| 1033 | EnergyStatistics_Config | U16 |  |  |  |  | RW | Register for statistics power return date. High byte: the time setting of the returned data. 0x01: Every day, the first 24 data in the return area are valid; 0x02: Every month, the first 31 data in the return area are valid; 0x03: Every year, the first 12 data in the return area are valid; 0x04: life cycle, the first 20 data in the return area are valid; Other: invalid. Low byte: the setting of the returned data. 0x01: photovoltaic generation; 0x02: load consumption; 0x03: electricity Purchased from Grid ; 0x04: electricity sold to grid; 0x05: battery charging power; 0x06: battery discharging power; Other: invalid. | Installer
| 1034 | Language | U16 |  |  | 0 | 65535 | RW | Register for language setting | End User
| 1035 | Parallel_Control | U16 |  |  | 0 | 2 | RW | 0: Disable the inverters' parallel function 1: Enable the inverters' parallel function | Installer
| 1036 | Parallel_Master_Slave | U16 |  |  | 0 | 1 | RW | Configuration 0: Slave 1:Master | Installer
| 1037 | Parallel_Address | U16 |  |  | 0 | 10 | RW | Parallel address | Installer
| 1038 | UnbalancedSupport_Control | U16 |  |  | 0 | 1 | RW | 3-phase 4-wire mode grid unbalanced support control register 0: Disable unbalanced support function (default) 1: Enable unbalanced support function | Installer
| 1039 | PV_Generation_Ratio | U16 | 0.001 | p.u. | 800 | 3600 | RW | Generated power Rate, Default value 1000 | Installer
| 103A | Energy_Purchase_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Import power Rate, Default Value 1000 | Installer
| 103B | Energy_Selling_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Export Power Rate, Default Value 1000 | Installer
| 103C | Bat_Charge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Battery Charging power Rate, Default Value 1000 | Installer
| 103D | Bat_Discharge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Battery Discharging Power, Default Value 1000 | Installer
| 103E | LogicInterface_Control | U16 |  |  | 0 | 1 | RW | Logical Interface Control Register 0: Disable 1: enable
103F
| 1040 | AddressMask_Config_Basic2 | U64 |  |  |  |  | R | Each Character in this field, will verify the validity of 64 addresses. Bit4 represents the address where the highest bit address of this field plus 1, 0 means invalid; 1 means valid. | End User
| 1041 | [8 empty] | End User
| 1042 | [8 empty] | End User
| 1043 | [8 empty] | End User
| 1044 | BatConfig_ID | U16 |  |  | 0 | 7 | RW | Battery serial number. The serial number specified by this register corresponds to the battery input interface of the inverter. After successfully writing to this register, the battery parameters will be updated to the parameters corresponding to the written serial number. | End User
| 1045 | BatConfig_Address | U16 |  |  | 0 | 99 | RW | Battery Communication Address, multiple battery connected in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
| 1046 | BatConfig_Potocol | U16 |  |  | 0 | 65535 | RW | Battery parameter-communication protocol 0: Sofar Built-in BMS 1:Pylontech's Protocol 2： Sofar's Protocol 3：Amass 4:LG 5:Alpha ESS 6.CATL 7.Weco 8：Fronus 9：EMS 10：Nilar | End User
| 1047 | BatConfig_Voltage_Over | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-Overvoltage protection | Installer
| 1048 | BatConfig_Voltage_Charge | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-Charge voltage protection | Installer
| 1049 | BatConfig_Voltage_Lack | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-undervoltage protection ,lead-acid battery visible | Installer
| 104A | BatConfig_Voltage_Discharge_Stop | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-Lowest discharge voltage | Installer
| 104B | BatConfig_Current_Charge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery Parameter-Maximum charge current limit | End User
| 104C | BatConfig_Current_Discharge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery Parameter-Maximum discharge current limit | End User
| 104D | BatConfig_Depth_of_Discharge | U16 | 1 | % | 1 | 90 | RW | Dod indicates the max discharge power, when SOC<1-DOD, inverter will stop power discharge , inverter will stop power discharge caused by other issues. DOD<=EOD | End User
| 104E | BatConfig_End_of_Discharge | U16 | 1 | % | 1 | 90 | RW | EOD indicate the max discharge power on off grid mode, when SOC<1-EOD, inverter will stop power discharge , inverter will stop power discharge caused by other issues. | End User
| 104F | BatConfig_Capacity | U16 | 1 | Ah | 1 | 65535 | RW | Battery Parameters-Capacity （Default 50） | End User
| 1050 | BatConfig_Voltage_Nominal | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameters-Rated Battery Voltage (Default 0） | End User
| 1051 | BatConfig_Cell_Type | U16 | 1 |  | 0 | 6 | RW | Battery Parameters_battery Type 0: Lead-acid(Default) 1: lithium iron phosphate Battery 2: Lithium Ternary Battery 3: lithium titanate Battery 4：AGM 5：Gel 6：Flooded | End User
| 1052 | BatConfig_EPS_Buffer | U16 | 1 | % | 5 | 100 | RW | Battery parameters-off-grid recovery discharge hysteresis; EPS_Buffer is not greater than EOD | End User
| 1053 | BatConfig_Control | U16 |  |  |  |  | RW | Battery parameters write in control. Input value is 1, the value of shadow register in battery parameters setting will upgrade to System battery parameter configuration .Input value is 2, the value of shadow register in battery parameters setting will upgrade to default value of BatConfig_Potocol . It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
| 1054 | BatConfig_Address2 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries connected in the system, this register used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
| 1055 | BatConfig_Address3 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries connected in the system, this register used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
| 1056 | BatConfig_Address4 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries connected in the system, this register used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
| 1057 | BatConfig_TEMPCO | I16 | 0.1 | mV/Cell | -60 | 0 | RW | Battery parameters-Lead-acid battery temperature compensation coefficient.
| 1058 | BatConfig_Voltage_Recovery_Buffer | U16 | 0.1 | V |  |  | RW | Battery parameters-Lead-acid battery recovery discharge voltage increment. For example: Stop discharging when the battery voltage < minimum discharge voltage".
| 1059 | BatConfig_Control_Bits | U16 |  |  |  |  | RW | Resume discharging when "battery voltage > minimum discharge voltage + resuming discharge voltage increment"."
| 105A | BatConfig_Voltage_Float | U16 | 0.1 | V |  |  | RW | Battery Parameters - Function Control Bits Bit0: SOC control disable (0: use SOC; 1: disable SOC)
105B
105C
105D
105E
105F
| 1060 | PCCSampleMode | U16 |  |  | 0 | 2 | RW | PCC power acquisition device configuration 0: not used 1: Electricity meter 2: CT 3: ARPC | End User
| 1061 | Resonance_Sensitivity | U16 |  |  | 1 | 100 | RW | Resonance detection sensitivity | End User
1062
1063
1064
1065
1066
1067
1068
1069
106A
106B
106C
106D
106E
106F
1070
1071
1072
1073
1074
1075
1076
1077
1078
1079
107A
107B
107C
107D
107E
107F
| 1080 | AddressMask_Config_Basic3 | U64 |  |  |  |  | R | Each Character in this field, will verify the validity of 64 addresses. Bit4 represents the address where the highest bit address of this field plus 1, 0 means invalid; 1 means valid. | Installer
| 1081 | [8 empty] | Installer
| 1082 | [8 empty] | Installer
| 1083 | [8 empty] | Installer
| 1084 | Arcing_Alarm_Enable | U16 |  |  |  |  | RW | Enable ARC testing | Installer
| 1085 | PeakToPeakSet | U16 | 1 |  | 0x64 |  | RW | Peak-to-peak setting | Installer
| 1086 | VarianceSet | U16 | 1 |  | 0x95 |  | RW | Variance setting | Installer
| 1087 | HarmonicEnergySet | U16 | 1 |  | 0x01 |  | RW | Harmonic energy setting | Installer
| 1088 | AmplitudeVarianceSet | U16 | 1 |  | 0x01 |  | RW | Magnitude variance setting | Installer
| 1089 | TimeDomWeiSet | U16 | 1 |  | 0x01 |  | RW | Time domain weight setting | Installer
| 108A | FreDomWeiSet | U16 | 1 |  | 0x05 |  | RW | Frequency domain weight setting | Installer
| 108B | ArcDetectSensitivity | U16 | 1 |  | 0x14 |  | RW | Arc detection sensitivity | Installer
| 108C | ArcAlarmShutdownThreshold | U16 | 1 |  | 0x05 |  | RW | Arc Alarm Count Shutdown Threshold | Installer
| 108D | ArcSelfCheckCommand | U16 |  |  | 0x01 |  | RW | Write 1 to start self-test (self-test all channels). Auto-zero at the end of self-test. | Installer
| 108E | ArcingAlarmClear | U16 | 1 |  | 0x1234 | 0x1234 | RW | Write 0x1234 to clear arc alarm (all channels) | Installer
| 108F | ArcAlarmCnt | U16 | 1 |  |  |  | RW | Arc Alarm Count | Installer
| 1090 | AfciResult | U16 | 1 |  |  |  | R | Handshake result | Installer
| 1091 | SelfCheckResult | U16 |  |  |  |  | R | Bit0-Channel 1 self-test result (0 self-test success; 1 self-test failure or no self-test) Bit1-Channel 2,Bit2-Channel 3,Bit3-Channel 4,Bit4-Channel 5,Bit5-Channel 6, | Installer
| 1092 | SelfCheckState | U16 |  |  |  |  | R | Channel self-test status 0: No self-test 1: Self-test in progress 2: Self-test completed | Installer
1093
1094
1095
1096
1097
1098
1099
109A
109B
109C
109D
109E
109F
| 10A0 | PLC_Enable_Setting | U16 |  |  |  |  | RW
| 10A1 | PLC_Com_Property | U16 | NULL | NULL | 0 |  | RW | bit0-bot1:0~1 corresponds to 1/1.5 Bit2~bit4:0~7 correspond to three verification methods: NONE/odd/EVEN bit5~bit7 0~3 corresponding to 8/9l two data bit lengths bit8~15 0~7 corresponding to 4800/9600/19200/38400/115200 | End User
10A2
10A3
10A4
| 10A5 | BLE_Enable_Setting | U16 | NULL | NULL | 0 | 1 | RW
| 10A6 | BLE_Com_Property | U16 | NULL | NULL | 0 | 65535 | RW | bit0-bot1:0~1 corresponds to 1/1.5 Bit2~bit4:0~7 correspond to three verification methods: NONE/odd/EVEN bit5~bit7 0~1 corresponding to 8/9l two data bit lengths bit8~15 0~7 corresponding to 4800/9600/19200/38400/115200
10A7
10A8
10A9
10AA
10AB
10AC
10AD
10AE
10AF
| 10B0 | PID_Auto_running_enable | U16 |  |  | 0 | 1 | RW | PID starts to run automatically. 0 means disabled; 1 means enabled. | End User
| 10B1 | PID_Working_Start_Time | BCD16 | 1 | Minute | 0 | 2359 | RW | PID work start time (BCD code). For example: the minimum value 0x0000 means 00:00; The maximum value of 0x2359 means 23:59. | End User
| 10B2 | PID_Working_Hours | U16 | 1 | Minute | 0 | 65535 | RW | PID working hours. | End User
| 10B3 | PID_Working_PV_Threshold | U16 | 0.1 | V | 0 | 65535 | RW | PID starts the PV value threshold. When the PV voltage is lower than the threshold value, PID is allowed to start. | End User
| 10B4 | PID_Break_Restart_Delay | U16 | 1 | Minute | 0 | 65535 | RW | Waiting time for restart after PID fault is closed. | End User
10B5
10B6
10B7
10B8
10B9
10BA
10BB
10BC
10BD
10BE
10BF
10C0
10C1
10C2
10C3
10C4
10C5
10C6
10C7
10C8
10C9
10CA
10CB
10CC
10CD
10CE
10CF
10D0
10D1
10D2
10D3
10D4
10D5
10D6
10D7
10D8
10D9
10DA
10DB
10DC
10DD
10DE
10DF
10E0
10E1
10E2
10E3
10E4
10E5
10E6
10E7
10E8
10E9
10EA
10EB
10EC
10ED
10EE
10EF
10F0
10F1
10F2
10F3
10F4
10F5
10F6
10F7
10F8
10F9
10FA
10FB
10FC
10FD
10FE
10FF
Remote control (0x1100-0x12FF)
| 1100 | AddressMask_Config_Remote1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
1101
1102
1103
| 1104 | Remote_On_Off_Control | U16 |  |  | 0 | 1 | RW | Remote power on/off. 0x0000: power off 0x0001: power on | End User
| 1105 | Power_Control | U16 |  |  |  |  | RWV | Power control. Bit0: active (address 0x1106) enable bit Bit1: Reactive (address 0x1107-0x1108) enable bit Bit2: Reactive mode selection bit (0: Reactive_Power; 1: Power_Factor) Bit3: SVG enable bit Bit4: SVG reactive mode selection bit (0: Fixed_Reactive_Power; 1: Reactive_Power) | End User
| 1106 | Active_Power_Export_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | Output maximum active power percentage | End User
| 1107 | Active_Power_Import_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | Input maximum active power percentage | End User
| 1108 | Reactive_Power_Setting | I16 | 0.1 | % | -1000 | 1000 | RWV | Percentage of reactive power. Note: The maximum reactive power is limited by the specific model. | End User
| 1109 | Power_Factor_Setting | I16 | 0.01 | p.u. | -100 | 100 | RWV | Power factor. Note: The minimum power factor is limited by the specific model. | End User
| 110A | Active_Power_Limit_Speed | U16 | 1 | % | 1 | 65535 | RWV | Active power limit change rate | End User
| 110B | Reactive_Power_Response_Time | U16 | 0.1 | second | 0 | 65535 | RWV | Reactive power setting response time | End User
| 110C | SVG_Fixed_Reactive_Power_Setting | I16 | 0.1 | kVar | -32768 | 32767 | RWV | Fixed reactive power magnitude in SVG mode | End User
| 110D | [8 empty] | End User
| 110E | [8 empty] | End User
| 110F | [8 empty] | End User
| 1110 | Energy_Storage_Mode_Control | U16 |  |  | 0 | 4 | RW | Energy storage working mode setting; 0: Spontaneous self-use mode 1: Time-of-use electricity price model 2: Timing charging and discharging mode 3: Passive mode 4: Peak clipping mode 5: Off-grid mode 6：Generator mode Used to change the working mode. | End User
| 1111 | Timing_ID | U16 |  |  | 0 | 3 | RW | Timed charging and discharging-rule number; The smaller the serial number, the higher the priority. After successfully writing to this register, the timing charge and discharge parameters will be updated to the parameters corresponding to the written serial number. | End User
| 1112 | Timing_On_Off_Control | U16 |  |  | 0 | 1 | RW | Timing charge and discharge-enable control; Bit0: charge enable Bit1: Discharge enable | End User
| 1113 | Timing_Charge_Start | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging start hour Low byte. Charging start minutes | End User
| 1114 | Timing_Charge_End | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging end hour Low byte. Minutes after charging | End User
| 1115 | Timing_Discharge_Start | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Discharge start hour Low byte. Discharge start minute | End User
| 1116 | Timing_Discharge_End | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. End of discharge hour Low byte. Minutes after discharge | End User
| 1117 | Timing_Power_Charge | U32 | 1 | W | 1 | 4294967296 | RW | Timed charging and discharging-charging power | End User
| 1118 | [8 empty] | End User
| 1119 | Timing_Power_Discharge | U32 | 1 | W | 1 | 4294967296 | RW | Timing charge and discharge-discharge power | End User
| 111A | [8 empty] | End User
| 111B | Timing_Rsvd1 | [6 empty] | Timed charge and discharge-reserved 1 | End User
| 111C | Timing_Rsvd2 | [6 empty] | Timed charge and discharge-reserved 2 | End User
| 111D | Timing_Rsvd3 | [6 empty] | Timed charge and discharge-reserved 3 | End User
| 111E | Timing_Rsvd4 | [6 empty] | Timed charge and discharge-reserved 4 | End User
| 111F | Timing_Control | U16 |  |  | 1 | 1 | RW | Timing charge and discharge write control; When the written value is 1, the value in the shadow register of timing charge and discharge is updated to the system timing charge and discharge configuration; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, and the input parameters are incorrect | End User
1120 | 1120 | TOU_ID | U16 |  |  | 0 | 7 | RW | Time-of-use electricity price-rule number; The smaller the serial number, the higher the priority. After successfully writing to this register, the time-of-use electricity price parameter will be updated to the parameter corresponding to the written serial number. | End User
1121 | 1121 | TOU_On_Off_Control | U16 |  |  | 0 | 1 | RW | Time-of-use price-rule enable; 0: disabled 1: enable | End User
1122 | 1122 | TOU_Charge_Start | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging start hour Low byte. Charging start minutes | End User
1123 | 1123 | TOU_Charge_End | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging end hour Low byte. Minutes after charging | End User
1124 | 1124 | TOU_Charge_Target_SOC | U16 | 1 | % | 30 | 100 | RW | Time-of-use price-mandatory charging cut-off SOC; The percentage of remaining power. When the current SOC of the battery reaches the value of this register, the forced charging ends and enters the spontaneous self-use mode, while discharging is prohibited. | End User
1125 | 1125 | TOU_Charge_Power | U32 | 1 | W | 1 | 4294967296 | RW | Time-of-use price-mandatory charging power; The set value cannot exceed the rated power of the machine. | End User
1126 | 1126
1127 | 1127 | TOU_Executed_Date_Start | U16 | 1 1 | Month Date | 1 1 | 12 31 | RW | High byte. The month when the rule becomes effective Low byte. Effective date of the rule | End User
1128 | 1128 | TOU_Executed_Date_End | U16 | 1 1 | Month Date | 1 1 | 12 31 | RW | High byte. The month when the rule ceases to take effect Low byte. The date when the rule ceases to take effect | End User
1129 | 1129 | TOU_Executed_Day_of_Week | U16 |  |  |  |  | RW | Time-of-use electricity price-week when the rule takes effect; This register is represented by a bit field, a bit of 0 indicates an invalid day of the week, and a bit of 1 indicates a valid day of the week Bit0: Monday Bit1: Tuesday Bit2: Wednesday Bit3: Thursday Bit4: Friday Bit5: Saturday Bit6: Sunday | Installer
| 112A | TOU_Rsvd1 | [6 empty] | Time-of-use energy price-reserved 1 | End User
| 112B | TOU_Rsvd2 | [6 empty] | Time-of-use energy price-reserved 2 | End User
| 112C | TOU_Rsvd3 | [6 empty] | Time-of-use energy price-reserved 3 | End User
| 112D | TOU_Rsvd4 | [6 empty] | Time-of-use energy price-reserved 4 | End User
| 112E | TOU_Rsvd5 | [6 empty] | Time-of-use energy price-reserved 5 | End User
| 112F | TOU_Control | U16 |  |  | 1 | 1 | RW | Time-of-use energy price-write control; When the written value is 1, the value in the shadow register of the time-of-use electricity price is updated to the system time-of-use electricity price configuration; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, and the input parameters are incorrect | End User
| 1130 | Peak_Shaving_Discharge_Threshold | U32 | 1 | W | 100 |  | RW | The power limit that allows the system to buy electricity from the grid | End User
| 1131 | [8 empty] | End User
| 1132 | Peak_Shaving_Charge_Threshold | U32 | 1 | W | 100 |  | RW | The power cap that allows the system to sell electricity to the grid | End User
| 1133 | [8 empty] | End User
1134
1135
1136
1137
1138
1139
113A
113B
113C
113D
113E
113F
| 1140 | AddressMask_Config_Remote2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
1141
1142
1143
| 1144 | Off_Grid_Charge_Source | U16 |  |  | 0 | 2 | RW | Off-grid mode-charging source selection: 0: Grid 1: Generator 2: reserved
| 1145 | Off_Grid_Grid_Power | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode-power drawn from the grid
| 1146 | Off_Grid_DG_Power | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode-generator power
1147
1148
1149
114A
114B
114C
114D
114E
114F
1150
1151
1152
1153
1154
1155
1156
1157
1158
1159
115A
115B
115C
115D
115E
115F
1160
1161
1162
1163
1164
1165
1166
1167
1168
1169
116A
116B
116C
116D
116E
116F
1170
1171
1172
1173
1174
1175
1176
1177
1178
1179
117A
117B
117C
117D
117E
117F
| 1180 | AddressMask_Config_Remote3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
| 1181 | [8 empty] | End User
| 1182 | [8 empty] | End User
| 1183 | [8 empty] | End User
| 1184 | Passive_Timeout | U16 | 1 | Second | 0 | 65535 | RW | Passive mode-timeout control; Default value: 0; Set the passive mode communication timeout time. When the inverter does not receive any communication within the time set by this register, the inverter will force the timeout action. In particular, writing 0 to this register will disable the timeout function. | End User
| 1185 | Passive_Timeout_Action | U16 |  |  | 0 | 1 | RW | Passive mode-timeout action; 0: Forced standby 1: Forced to restore to the energy storage mode before entering the passive mode | End User
| 1186 | Passive_Rsvd1 | [6 empty] | Passive mode-reserved 1 | End User
| 1187 | Passive_Manual_Gdes | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode expected grid power (Gdes); A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 1188 | [8 empty] | End User
| 1189 | Passive_Manual_Blo | I32 | 1 | W | -2147483648 | 2147483647 | RW | The minimum charge and discharge power of the battery in Manual mode (Blo); Positive value means charging; Negative values indicate discharge. | End User
| 118A | [8 empty] | End User
| 118B | Passive_Manual_Bup | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Manual mode (Bup); Positive value means charging; Negative values indicate discharge. | End User
| 118C | [8 empty] | End User
| 118D | Passive_Manual_Gdzup | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows selling electric power (Gdzup); A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 118E | [8 empty] | End User
| 118F | Passive_Manual_Gdzlo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows to buy electric power (Gdzlo); A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 1190 | [8 empty] | End User
| 1191 | Passive_Scheduler_Gdes_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 1192 | [8 empty] | End User
| 1193 | Passive_Scheduler_Blo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | The minimum charge and discharge power of the battery in Scheduler mode (Blo_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 1194 | [8 empty] | End User
| 1195 | Passive_Scheduler_Bup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Scheduler mode (Bup_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 1196 | [8 empty] | End User
| 1197 | Passive_Scheduler_Gdzup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to sell electric power (Gdzup_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 1198 | [8 empty] | End User
| 1199 | Passive_Scheduler_Gdzlo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 119A | [8 empty] | End User
| 119B | Passive_Scheduler_Gdes_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 119C | [8 empty] | End User
| 119D | Passive_Scheduler_Blo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | The minimum charge and discharge power of the battery in Scheduler mode (Blo_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 119E | [8 empty] | End User
| 119F | Passive_Scheduler_Bup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Scheduler mode (Bup_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 11A0 | [8 empty] | End User
| 11A1 | Passive_Scheduler_Gdzup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to sell electric power (Gdzup_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 11A2 | [8 empty] | End User
| 11A3 | Passive_Scheduler_Gdzlo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
| 11A4 | [8 empty] | End User
| 11A5 | Passive_Scheduler_StartTime | U32 | 1 | Second | 0 | 4294967296 | RW | Scheduler mode application expectation parameter setting value start time; StartTime is in unix time format. Since the internal time of the system defaults to Greenwich Mean Time (GMT), when setting this parameter, you should pay attention to the local time zone of your country, StartTime=(local Unix Time)±(local time and UTC/GMT The number of seconds corresponding to the time difference) | End User
| 11A6 | [8 empty] | End User
| 11A7 | Passive_Scheduler_DurationTime | U32 | 1 | Second | 0 | 4294967296 | RW | Scheduler mode application expects the duration of the parameter setting value (DurationTime) | End User
| 11A8 | [8 empty] | End User
| 11A9 | Passive_Scheduler_ManagementMode | U16 |  |  | 0 | 2 | RW | Scheduler mode management mode selection (ManagementMode); 0: Spontaneous self-use mode 1: Manual mode 2: Scheduler mode Only 0, 1, 2 can be input, other data is invalid. | End User
11AA
11AB
11AC
11AD
11AE
11AF
11B0
11B1
11B2
11B3
11B4
11B5
11B6
11B7
11B8
11B9
11BA
11BB
11BC
11BD
11BE
11BF
| 11C0 | AddressMask_Config_Remote4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
| 11C1 | [8 empty] | End User
| 11C2 | [8 empty] | End User
| 11C3 | [8 empty] | End User
11C4
11C5
The inverter returns a read-only result (0x1300-0x15FF)
| 1300 | AddressMask_Config_ReadOnly_Result1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
1301
1302
1303
| 1304 | Italay_Autotest_Result1 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. The first-level overvoltage protection value is set by default.
| 1305 | Italay_Autotest_Result2 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. The first-level overvoltage protection time is set by default.
| 1306 | Italay_Autotest_Result3 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. Test result of level 1 overvoltage protection value.
| 1307 | Italay_Autotest_Result4 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. The first level overvoltage protection time test result.
| 1308 | Italay_Autotest_Result5 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. The secondary overvoltage protection value is set by default.
| 1309 | Italay_Autotest_Result6 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. The second-level overvoltage protection time is set by default.
| 130A | Italay_Autotest_Result7 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. Test result of secondary overvoltage protection value.
| 130B | Italay_Autotest_Result8 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. Test result of secondary overvoltage protection time.
| 130C | Italay_Autotest_Result9 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. The first-level undervoltage protection value is set by default.
| 130D | Italay_Autotest_Result10 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s1. The first-level undervoltage protection time is set by default.
| 130E | Italay_Autotest_Result11 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. The first level undervoltage protection value test result.
| 130F | Italay_Autotest_Result12 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s1. The first level undervoltage protection time test result.
| 1310 | Italay_Autotest_Result13 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s2. The secondary undervoltage protection value is set by default.
| 1311 | Italay_Autotest_Result14 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s2. The second level undervoltage protection time is set by default.
| 1312 | Italay_Autotest_Result15 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s2. Test result of secondary undervoltage protection value.
| 1313 | Italay_Autotest_Result16 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s2. Test result of secondary undervoltage protection time.
| 1314 | Italay_Autotest_Result17 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s1. The first-level over-frequency protection value is set by default.
| 1315 | Italay_Autotest_Result18 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s1. The first-level over-frequency protection time is set by default.
| 1316 | Italay_Autotest_Result19 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s1. Test result of level 1 over-frequency protection value.
| 1317 | Italay_Autotest_Result20 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s1. The first level over-frequency protection time test result.
| 1318 | Italay_Autotest_Result21 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s2. The second-level over-frequency protection value is set by default.
| 1319 | Italay_Autotest_Result22 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s2. The second level over-frequency protection time is set by default.
| 131A | Italay_Autotest_Result23 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s2. Test result of secondary over-frequency protection value.
| 131B | Italay_Autotest_Result24 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s2. Test result of secondary over-frequency protection time.
| 131C | Italay_Autotest_Result25 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s1. The first level under-frequency protection value is set by default.
| 131D | Italay_Autotest_Result26 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s1. The first level under-frequency protection time is set by default.
| 131E | Italay_Autotest_Result27 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s1. Test result of first-level under-frequency protection value.
| 131F | Italay_Autotest_Result28 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s1. The first level under-frequency protection time test result.
| 1320 | Italay_Autotest_Result29 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s2. The second-level under-frequency protection value is set by default.
| 1321 | Italay_Autotest_Result30 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s2. The second level under-frequency protection time is set by default.
| 1322 | Italay_Autotest_Result31 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s2. Test result of secondary underfrequency protection value.
| 1323 | Italay_Autotest_Result32 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s2. Test result of secondary under-frequency protection time.
| 1324 | Italay_Autotest_Result33 | [6 empty] | Italy automatic test result 33
| 1325 | Italay_Autotest_Result34 | [6 empty] | Italy automatic test result 34
| 1326 | Italay_Autotest_Result35 | [6 empty] | Italy automatic test result 35
| 1327 | Italay_Autotest_Result36 | [6 empty] | Italy automatic test result 36
| 1328 | Italay_Autotest_Result37 | [6 empty] | Italy automatic test result 37
| 1329 | Italay_Autotest_Result38 | [6 empty] | Italy automatic test result 38
| 132A | Italay_Autotest_Result39 | [6 empty] | Italy automatic test result 39
| 132B | Italay_Autotest_Result40 | [6 empty] | Italian automatic test result 40
| 132C | Italay_Autotest_Result41 | [6 empty] | Italian automatic test result 41
| 132D | Italay_Autotest_Result42 | [6 empty] | Italian automatic test result 42
| 132E | Italay_Autotest_Result43 | [6 empty] | Italy automatic test result 43
| 132F | Italay_Autotest_Result44 | [6 empty] | Italy automatic test result 44
| 1330 | Italay_Autotest_Result45 | [6 empty] | Italy automatic test result 45
| 1331 | Italay_Autotest_Result46 | [6 empty] | Italy automatic test result 46
| 1332 | Italay_Autotest_Result47 | [6 empty] | Italy automatic test result 47
| 1333 | Italay_Autotest_Result48 | [6 empty] | Italy automatic test result 48
| 1340 | AddressMask_Config_ReadOnly_Result2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
1341
1342
1343
| 1344 | IVCurve_Voltage1 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 1
| 1345 | IVCurve_Current1 | U16 | 0.01 | A |  |  | R | IV curve sweep current 1
| 1346 | IVCurve_Voltage2 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 2
| 1347 | IVCurve_Current2 | U16 | 0.01 | A |  |  | R | IV curve scan current 2
| 1348 | IVCurve_Voltage3 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 3
| 1349 | IVCurve_Current3 | U16 | 0.01 | A |  |  | R | IV curve scan current 3
| 134A | IVCurve_Voltage4 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 4
| 134B | IVCurve_Current4 | U16 | 0.01 | A |  |  | R | IV curve scan current 4
| 134C | IVCurve_Voltage5 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 5
| 134D | IVCurve_Current5 | U16 | 0.01 | A |  |  | R | IV curve scan current 5
| 134E | IVCurve_Voltage6 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 6
| 134F | IVCurve_Current6 | U16 | 0.01 | A |  |  | R | IV curve scan current 6
| 1350 | IVCurve_Voltage7 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 7
| 1351 | IVCurve_Current7 | U16 | 0.01 | A |  |  | R | IV curve scan current 7
| 1352 | IVCurve_Voltage8 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 8
| 1353 | IVCurve_Current8 | U16 | 0.01 | A |  |  | R | IV curve scan current 8
| 1354 | IVCurve_Voltage9 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 9
| 1355 | IVCurve_Current9 | U16 | 0.01 | A |  |  | R | IV curve sweep current 9
| 1356 | IVCurve_Voltage10 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 10
| 1357 | IVCurve_Current10 | U16 | 0.01 | A |  |  | R | IV curve sweep current 10
| 1358 | IVCurve_Voltage11 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 11
| 1359 | IVCurve_Current11 | U16 | 0.01 | A |  |  | R | IV curve scan current 11
| 135A | IVCurve_Voltage12 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 12
| 135B | IVCurve_Current12 | U16 | 0.01 | A |  |  | R | IV curve scan current 12
| 135C | IVCurve_Voltage13 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 13
| 135D | IVCurve_Current13 | U16 | 0.01 | A |  |  | R | IV curve sweep current 13
| 135E | IVCurve_Voltage14 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 14
| 135F | IVCurve_Current14 | U16 | 0.01 | A |  |  | R | IV curve scan current 14
| 1360 | IVCurve_Voltage15 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 15
| 1361 | IVCurve_Current15 | U16 | 0.01 | A |  |  | R | IV curve scan current 15
| 1362 | IVCurve_Voltage16 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 16
| 1363 | IVCurve_Current16 | U16 | 0.01 | A |  |  | R | IV curve scan current 16
| 1364 | IVCurve_Voltage17 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 17
| 1365 | IVCurve_Current17 | U16 | 0.01 | A |  |  | R | IV curve scan current 17
| 1366 | IVCurve_Voltage18 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 18
| 1367 | IVCurve_Current18 | U16 | 0.01 | A |  |  | R | IV curve scan current 18
| 1368 | IVCurve_Voltage19 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 19
| 1369 | IVCurve_Current19 | U16 | 0.01 | A |  |  | R | IV curve scan current 19
| 136A | IVCurve_Voltage20 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 20
| 136B | IVCurve_Current20 | U16 | 0.01 | A |  |  | R | IV curve scan current 20
| 136C | IVCurve_Voltage21 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 21
| 136D | IVCurve_Current21 | U16 | 0.01 | A |  |  | R | IV curve scan current 21
| 136E | IVCurve_Voltage22 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 22
| 136F | IVCurve_Current22 | U16 | 0.01 | A |  |  | R | IV curve scan current 22
| 1370 | IVCurve_Voltage23 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 23
| 1371 | IVCurve_Current23 | U16 | 0.01 | A |  |  | R | IV curve scan current 23
| 1372 | IVCurve_Voltage24 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 24
| 1373 | IVCurve_Current24 | U16 | 0.01 | A |  |  | R | IV curve scan current 24
| 1374 | IVCurve_Voltage25 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 25
| 1375 | IVCurve_Current25 | U16 | 0.01 | A |  |  | R | IV curve scan current 25
| 1376 | IVCurve_Voltage26 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 26
| 1377 | IVCurve_Current26 | U16 | 0.01 | A |  |  | R | IV curve scan current 26
| 1378 | IVCurve_Voltage27 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 27
| 1379 | IVCurve_Current27 | U16 | 0.01 | A |  |  | R | IV curve scan current 27
| 137A | IVCurve_Voltage28 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 28
| 137B | IVCurve_Current28 | U16 | 0.01 | A |  |  | R | IV curve scan current 28
| 137C | IVCurve_Voltage29 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 29
| 137D | IVCurve_Current29 | U16 | 0.01 | A |  |  | R | IV curve scan current 29
| 137E | IVCurve_Voltage30 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 30
| 137F | IVCurve_Current30 | U16 | 0.01 | A |  |  | R | IV curve scan current 30
| 1380 | AddressMask_Config_ReadOnly_Result3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid
1381
1382
1383
| 1384 | IVCurve_Voltage31 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 31
| 1385 | IVCurve_Current31 | U16 | 0.01 | A |  |  | R | IV curve scan current 31
| 1386 | IVCurve_Voltage32 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 32
| 1387 | IVCurve_Current32 | U16 | 0.01 | A |  |  | R | IV curve scan current 32
| 1388 | IVCurve_Voltage33 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 33
| 1389 | IVCurve_Current33 | U16 | 0.01 | A |  |  | R | IV curve scan current 33
| 138A | IVCurve_Voltage34 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 34
| 138B | IVCurve_Current34 | U16 | 0.01 | A |  |  | R | IV curve scan current 34
| 138C | IVCurve_Voltage35 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 35
| 138D | IVCurve_Current35 | U16 | 0.01 | A |  |  | R | IV curve scan current 35
| 138E | IVCurve_Voltage36 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 36
| 138F | IVCurve_Current36 | U16 | 0.01 | A |  |  | R | IV curve scan current 36
| 1390 | IVCurve_Voltage37 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 37
| 1391 | IVCurve_Current37 | U16 | 0.01 | A |  |  | R | IV curve scan current 37
| 1392 | IVCurve_Voltage38 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 38
| 1393 | IVCurve_Current38 | U16 | 0.01 | A |  |  | R | IV curve scan current 38
| 1394 | IVCurve_Voltage39 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 39
| 1395 | IVCurve_Current39 | U16 | 0.01 | A |  |  | R | IV curve scan current 39
| 1396 | IVCurve_Voltage40 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 40
| 1397 | IVCurve_Current40 | U16 | 0.01 | A |  |  | R | IV curve scan current 40
| 1398 | IVCurve_Voltage41 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 41
| 1399 | IVCurve_Current41 | U16 | 0.01 | A |  |  | R | IV curve scan current 41
| 139A | IVCurve_Voltage42 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 42
| 139B | IVCurve_Current42 | U16 | 0.01 | A |  |  | R | IV curve scan current 42
| 139C | IVCurve_Voltage43 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 43
| 139D | IVCurve_Current43 | U16 | 0.01 | A |  |  | R | IV curve scan current 43
| 139E | IVCurve_Voltage44 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 44
| 139F | IVCurve_Current44 | U16 | 0.01 | A |  |  | R | IV curve scan current 44
| 13A0 | IVCurve_Voltage45 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 45
| 13A1 | IVCurve_Current45 | U16 | 0.01 | A |  |  | R | IV curve scan current 45
| 13A2 | IVCurve_Voltage46 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 46
| 13A3 | IVCurve_Current46 | U16 | 0.01 | A |  |  | R | IV curve scan current 46
| 13A4 | IVCurve_Voltage47 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 47
| 13A5 | IVCurve_Current47 | U16 | 0.01 | A |  |  | R | IV curve scan current 47
| 13A6 | IVCurve_Voltage48 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 48
| 13A7 | IVCurve_Current48 | U16 | 0.01 | A |  |  | R | IV curve scan current 48
| 13A8 | IVCurve_Voltage49 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 49
| 13A9 | IVCurve_Current49 | U16 | 0.01 | A |  |  | R | IV curve scan current 49
| 13AA | IVCurve_Voltage50 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 50
| 13AB | IVCurve_Current50 | U16 | 0.01 | A |  |  | R | IV curve scan current 50
| 13AC | IVCurve_Voltage51 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 51
| 13AD | IVCurve_Current51 | U16 | 0.01 | A |  |  | R | IV curve scan current 51
| 13AE | IVCurve_Voltage52 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 52
| 13AF | IVCurve_Current52 | U16 | 0.01 | A |  |  | R | IV curve scan current 52
| 13B0 | IVCurve_Voltage53 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 53
| 13B1 | IVCurve_Current53 | U16 | 0.01 | A |  |  | R | IV curve scan current 53
| 13B2 | IVCurve_Voltage54 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 54
| 13B3 | IVCurve_Current54 | U16 | 0.01 | A |  |  | R | IV curve scan current 54
| 13B4 | IVCurve_Voltage55 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 55
| 13B5 | IVCurve_Current55 | U16 | 0.01 | A |  |  | R | IV curve scan current 55
| 13B6 | IVCurve_Voltage56 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 56
| 13B7 | IVCurve_Current56 | U16 | 0.01 | A |  |  | R | IV curve scan current 56
| 13B8 | IVCurve_Voltage57 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 57
| 13B9 | IVCurve_Current57 | U16 | 0.01 | A |  |  | R | IV curve scan current 57
| 13BA | IVCurve_Voltage58 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 58
| 13BB | IVCurve_Current58 | U16 | 0.01 | A |  |  | R | IV curve scan current 58
| 13BC | IVCurve_Voltage59 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 59
| 13BD | IVCurve_Current59 | U16 | 0.01 | A |  |  | R | IV curve scan current 59
| 13BE | IVCurve_Voltage60 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 60
| 13BF | IVCurve_Current60 | U16 | 0.01 | A |  |  | R | IV curve scan current 60
| 13C0 | AddressMask_Config_ReadOnly_Result4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid
13C1
13C2
13C3
| 13C4 | IVCurve_Voltage61 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 61
| 13C5 | IVCurve_Current61 | U16 | 0.01 | A |  |  | R | IV curve scan current 61
| 13C6 | IVCurve_Voltage62 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 62
| 13C7 | IVCurve_Current62 | U16 | 0.01 | A |  |  | R | IV curve scan current 62
| 13C8 | IVCurve_Voltage63 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 63
| 13C9 | IVCurve_Current63 | U16 | 0.01 | A |  |  | R | IV curve scan current 63
| 13CA | IVCurve_Voltage64 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 64
| 13CB | IVCurve_Current64 | U16 | 0.01 | A |  |  | R | IV curve scan current 64
| 13CC | IVCurve_Voltage65 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 65
| 13CD | IVCurve_Current65 | U16 | 0.01 | A |  |  | R | IV curve scan current 65
| 13CE | IVCurve_Voltage66 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 66
| 13CF | IVCurve_Current66 | U16 | 0.01 | A |  |  | R | IV curve scan current 66
| 13D0 | IVCurve_Voltage67 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 67
| 13D1 | IVCurve_Current67 | U16 | 0.01 | A |  |  | R | IV curve scan current 67
| 13D2 | IVCurve_Voltage68 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 68
| 13D3 | IVCurve_Current68 | U16 | 0.01 | A |  |  | R | IV curve scan current 68
| 13D4 | IVCurve_Voltage69 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 69
| 13D5 | IVCurve_Current69 | U16 | 0.01 | A |  |  | R | IV curve scan current 69
| 13D6 | IVCurve_Voltage70 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 70
| 13D7 | IVCurve_Current70 | U16 | 0.01 | A |  |  | R | IV curve scan current 70
| 13D8 | IVCurve_Voltage71 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 71
| 13D9 | IVCurve_Current71 | U16 | 0.01 | A |  |  | R | IV curve scan current 71
| 13DA | IVCurve_Voltage72 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 72
| 13DB | IVCurve_Current72 | U16 | 0.01 | A |  |  | R | IV curve scan current 72
| 13DC | IVCurve_Voltage73 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 73
| 13DD | IVCurve_Current73 | U16 | 0.01 | A |  |  | R | IV curve scan current 73
| 13DE | IVCurve_Voltage74 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 74
| 13DF | IVCurve_Current74 | U16 | 0.01 | A |  |  | R | IV curve scan current 74
| 13E0 | IVCurve_Voltage75 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 75
| 13E1 | IVCurve_Current75 | U16 | 0.01 | A |  |  | R | IV curve scan current 75
| 13E2 | IVCurve_Voltage76 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 76
| 13E3 | IVCurve_Current76 | U16 | 0.01 | A |  |  | R | IV curve scan current 76
| 13E4 | IVCurve_Voltage77 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 77
| 13E5 | IVCurve_Current77 | U16 | 0.01 | A |  |  | R | IV curve scan current 77
| 13E6 | IVCurve_Voltage78 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 78
| 13E7 | IVCurve_Current78 | U16 | 0.01 | A |  |  | R | IV curve sweep current 78
| 13E8 | IVCurve_Voltage79 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 79
| 13E9 | IVCurve_Current79 | U16 | 0.01 | A |  |  | R | IV curve sweep current 79
| 13EA | IVCurve_Voltage80 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 80
| 13EB | IVCurve_Current80 | U16 | 0.01 | A |  |  | R | IV curve sweep current 80
| 13EC | IVCurve_Voltage81 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 81
| 13ED | IVCurve_Current81 | U16 | 0.01 | A |  |  | R | IV curve sweep current 81
| 13EE | IVCurve_Voltage82 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 82
| 13EF | IVCurve_Current82 | U16 | 0.01 | A |  |  | R | IV curve scan current 82
| 13F0 | IVCurve_Voltage83 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 83
| 13F1 | IVCurve_Current83 | U16 | 0.01 | A |  |  | R | IV curve sweep current 83
| 13F2 | IVCurve_Voltage84 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 84
| 13F3 | IVCurve_Current84 | U16 | 0.01 | A |  |  | R | IV curve sweep current 84
| 13F4 | IVCurve_Voltage85 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 85
| 13F5 | IVCurve_Current85 | U16 | 0.01 | A |  |  | R | IV curve sweep current 85
| 13F6 | IVCurve_Voltage86 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 86
| 13F7 | IVCurve_Current86 | U16 | 0.01 | A |  |  | R | IV curve scan current 86
| 13F8 | IVCurve_Voltage87 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 87
| 13F9 | IVCurve_Current87 | U16 | 0.01 | A |  |  | R | IV curve scan current 87
| 13FA | IVCurve_Voltage88 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 88
| 13FB | IVCurve_Current88 | U16 | 0.01 | A |  |  | R | IV curve sweep current 88
| 13FC | IVCurve_Voltage89 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 89
| 13FD | IVCurve_Current89 | U16 | 0.01 | A |  |  | R | IV curve scan current 89
| 13FE | IVCurve_Voltage90 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 90
| 13FF | IVCurve_Current90 | U16 | 0.01 | A |  |  | R | IV curve sweep current 90
| 1400 | AddressMask_Config_ReadOnly_Result5 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid.
1401
1402
1403
| 1404 | IVCurve_Voltage91 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 91
| 1405 | IVCurve_Current91 | U16 | 0.01 | A |  |  | R | IV curve sweep current 91
| 1406 | IVCurve_Voltage92 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 92
| 1407 | IVCurve_Current92 | U16 | 0.01 | A |  |  | R | IV curve scan current 92
| 1408 | IVCurve_Voltage93 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 93
| 1409 | IVCurve_Current93 | U16 | 0.01 | A |  |  | R | IV curve sweep current 93
| 140A | IVCurve_Voltage94 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 94
| 140B | IVCurve_Current94 | U16 | 0.01 | A |  |  | R | IV curve scan current 94
| 140C | IVCurve_Voltage95 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 95
| 140D | IVCurve_Current95 | U16 | 0.01 | A |  |  | R | IV curve sweep current 95
| 140E | IVCurve_Voltage96 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 96
| 140F | IVCurve_Current96 | U16 | 0.01 | A |  |  | R | IV curve scan current 96
| 1410 | IVCurve_Voltage97 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 97
| 1411 | IVCurve_Current97 | U16 | 0.01 | A |  |  | R | IV curve scan current 97
| 1412 | IVCurve_Voltage98 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 98
| 1413 | IVCurve_Current98 | U16 | 0.01 | A |  |  | R | IV curve scan current 98
| 1414 | IVCurve_Voltage99 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 99
| 1415 | IVCurve_Current99 | U16 | 0.01 | A |  |  | R | IV curve sweep current 99
| 1416 | IVCurve_Voltage100 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 100
| 1417 | IVCurve_Current100 | U16 | 0.01 | A |  |  | R | IV curve sweep current 100
| 1418 | IVCurve_Voltage101 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 101
| 1419 | IVCurve_Current101 | U16 | 0.01 | A |  |  | R | IV curve sweep current 101
| 141A | IVCurve_Voltage102 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 102
| 141B | IVCurve_Current102 | U16 | 0.01 | A |  |  | R | IV curve scan current 102
| 141C | IVCurve_Voltage103 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 103
| 141D | IVCurve_Current103 | U16 | 0.01 | A |  |  | R | IV curve scan current 103
| 141E | IVCurve_Voltage104 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 104
| 141F | IVCurve_Current104 | U16 | 0.01 | A |  |  | R | IV curve scan current 104
| 1420 | IVCurve_Voltage105 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 105
| 1421 | IVCurve_Current105 | U16 | 0.01 | A |  |  | R | IV curve scan current 105
| 1422 | IVCurve_Voltage106 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 106
| 1423 | IVCurve_Current106 | U16 | 0.01 | A |  |  | R | IV curve scan current 106
| 1424 | IVCurve_Voltage107 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 107
| 1425 | IVCurve_Current107 | U16 | 0.01 | A |  |  | R | IV curve scan current 107
| 1426 | IVCurve_Voltage108 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 108
| 1427 | IVCurve_Current108 | U16 | 0.01 | A |  |  | R | IV curve sweep current 108
| 1428 | IVCurve_Voltage109 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 109
| 1429 | IVCurve_Current109 | U16 | 0.01 | A |  |  | R | IV curve scan current 109
| 142A | IVCurve_Voltage110 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 110
| 142B | IVCurve_Current110 | U16 | 0.01 | A |  |  | R | IV curve scan current 110
| 142C | IVCurve_Voltage111 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 111
| 142D | IVCurve_Current111 | U16 | 0.01 | A |  |  | R | IV curve scan current 111
| 142E | IVCurve_Voltage112 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 112
| 142F | IVCurve_Current112 | U16 | 0.01 | A |  |  | R | IV curve scan current 112
| 1430 | IVCurve_Voltage113 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 113
| 1431 | IVCurve_Current113 | U16 | 0.01 | A |  |  | R | IV curve scan current 113
| 1432 | IVCurve_Voltage114 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 114
| 1433 | IVCurve_Current114 | U16 | 0.01 | A |  |  | R | IV curve sweep current 114
| 1434 | IVCurve_Voltage115 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 115
| 1435 | IVCurve_Current115 | U16 | 0.01 | A |  |  | R | IV curve sweep current 115
| 1436 | IVCurve_Voltage116 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 116
| 1437 | IVCurve_Current116 | U16 | 0.01 | A |  |  | R | IV curve scan current 116
| 1438 | IVCurve_Voltage117 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 117
| 1439 | IVCurve_Current117 | U16 | 0.01 | A |  |  | R | IV curve scan current 117
| 143A | IVCurve_Voltage118 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 118
| 143B | IVCurve_Current118 | U16 | 0.01 | A |  |  | R | IV curve scan current 118
| 143C | IVCurve_Voltage119 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 119
| 143D | IVCurve_Current119 | U16 | 0.01 | A |  |  | R | IV curve scan current 119
| 143E | IVCurve_Voltage120 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 120
| 143F | IVCurve_Current120 | U16 | 0.01 | A |  |  | R | IV curve sweep current 120
| 1440 | AddressMask_Config_ReadOnly_Result6 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid.
1441
1442
1443
| 1444 | IVCurve_Voltage121 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 121
| 1445 | IVCurve_Current121 | U16 | 0.01 | A |  |  | R | IV curve scan current 121
| 1446 | IVCurve_Voltage122 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 122
| 1447 | IVCurve_Current122 | U16 | 0.01 | A |  |  | R | IV curve scan current 122
| 1448 | IVCurve_Voltage123 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 123
| 1449 | IVCurve_Current123 | U16 | 0.01 | A |  |  | R | IV curve scan current 123
| 144A | IVCurve_Voltage124 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 124
| 144B | IVCurve_Current124 | U16 | 0.01 | A |  |  | R | IV curve scan current 124
| 144C | IVCurve_Voltage125 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 125
| 144D | IVCurve_Current125 | U16 | 0.01 | A |  |  | R | IV curve sweep current 125
| 144E | IVCurve_Voltage126 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 126
| 144F | IVCurve_Current126 | U16 | 0.01 | A |  |  | R | IV curve scan current 126
| 1450 | IVCurve_Voltage127 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 127
| 1451 | IVCurve_Current127 | U16 | 0.01 | A |  |  | R | IV curve scan current 127
| 1452 | IVCurve_Voltage128 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 128
| 1453 | IVCurve_Current128 | U16 | 0.01 | A |  |  | R | IV curve scan current 128
| 1454 | IVCurve_Voltage129 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 129
| 1455 | IVCurve_Current129 | U16 | 0.01 | A |  |  | R | IV curve scan current 129
| 1456 | IVCurve_Voltage130 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 130
| 1457 | IVCurve_Current130 | U16 | 0.01 | A |  |  | R | IV curve scan current 130
| 1458 | IVCurve_Voltage131 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 131
| 1459 | IVCurve_Current131 | U16 | 0.01 | A |  |  | R | IV curve scan current 131
| 145A | IVCurve_Voltage132 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 132
| 145B | IVCurve_Current132 | U16 | 0.01 | A |  |  | R | IV curve scan current 132
| 145C | IVCurve_Voltage133 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 133
| 145D | IVCurve_Current133 | U16 | 0.01 | A |  |  | R | IV curve scan current 133
| 145E | IVCurve_Voltage134 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 134
| 145F | IVCurve_Current134 | U16 | 0.01 | A |  |  | R | IV curve scan current 134
| 1460 | IVCurve_Voltage135 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 135
| 1461 | IVCurve_Current135 | U16 | 0.01 | A |  |  | R | IV curve scan current 135
| 1462 | IVCurve_Voltage136 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 136
| 1463 | IVCurve_Current136 | U16 | 0.01 | A |  |  | R | IV curve scan current 136
| 1464 | IVCurve_Voltage137 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 137
| 1465 | IVCurve_Current137 | U16 | 0.01 | A |  |  | R | IV curve scan current 137
| 1466 | IVCurve_Voltage138 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 138
| 1467 | IVCurve_Current138 | U16 | 0.01 | A |  |  | R | IV curve scan current 138
| 1468 | IVCurve_Voltage139 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 139
| 1469 | IVCurve_Current139 | U16 | 0.01 | A |  |  | R | IV curve scan current 139
| 146A | IVCurve_Voltage140 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 140
| 146B | IVCurve_Current140 | U16 | 0.01 | A |  |  | R | IV curve sweep current 140
| 146C | IVCurve_Voltage141 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 141
| 146D | IVCurve_Current141 | U16 | 0.01 | A |  |  | R | IV curve scan current 141
| 146E | IVCurve_Voltage142 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 142
| 146F | IVCurve_Current142 | U16 | 0.01 | A |  |  | R | IV curve scan current 142
| 1470 | IVCurve_Voltage143 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 143
| 1471 | IVCurve_Current143 | U16 | 0.01 | A |  |  | R | IV curve scan current 143
| 1472 | IVCurve_Voltage144 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 144
| 1473 | IVCurve_Current144 | U16 | 0.01 | A |  |  | R | IV curve scan current 144
| 1474 | IVCurve_Voltage145 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 145
| 1475 | IVCurve_Current145 | U16 | 0.01 | A |  |  | R | IV curve scan current 145
| 1476 | IVCurve_Voltage146 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 146
| 1477 | IVCurve_Current146 | U16 | 0.01 | A |  |  | R | IV curve scan current 146
| 1478 | IVCurve_Voltage147 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 147
| 1479 | IVCurve_Current147 | U16 | 0.01 | A |  |  | R | IV curve scan current 147
| 147A | IVCurve_Voltage148 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 148
| 147B | IVCurve_Current148 | U16 | 0.01 | A |  |  | R | IV curve scan current 148
| 147C | IVCurve_Voltage149 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 149
| 147D | IVCurve_Current149 | U16 | 0.01 | A |  |  | R | IV curve scan current 149
| 147E | IVCurve_Voltage150 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 150
| 147F | IVCurve_Current150 | U16 | 0.01 | A |  |  | R | IV curve scan current 150
| 1480 | HistoryEventList_ID1 | U16 |  |  |  |  | R | The latest 1st item of historical event ID
| 1481 | HistoryEventList_yM1 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1482 | HistoryEventList_dH1 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1483 | HistoryEventList_ms1 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1484 | HistoryEventList_ID2 | U16 |  |  |  |  | R | The 2nd most recent historical event ID
| 1485 | HistoryEventList_yM2 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1486 | HistoryEventList_dH2 | U16 |  |  |  |  | R | High byte: date; Low byte: hour. "
| 1487 | HistoryEventList_ms2 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1488 | HistoryEventList_ID3 | U16 |  |  |  |  | R | The 3rd most recent historical event ID
| 1489 | HistoryEventList_yM3 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 148A | HistoryEventList_dH3 | U16 |  |  |  |  | R | High byte: date; Low byte: hour. "
| 148B | HistoryEventList_ms3 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 148C | HistoryEventList_ID4 | U16 |  |  |  |  | R | The 4th most recent historical event ID
| 148D | HistoryEventList_yM4 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 148E | HistoryEventList_dH4 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 148F | HistoryEventList_ms4 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1490 | HistoryEventList_ID5 | U16 |  |  |  |  | R | The 5th most recent historical event ID
| 1491 | HistoryEventList_yM5 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1492 | HistoryEventList_dH5 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1493 | HistoryEventList_ms5 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1494 | HistoryEventList_ID6 | U16 |  |  |  |  | R | The 6th most recent historical event ID
| 1495 | HistoryEventList_yM6 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1496 | HistoryEventList_dH6 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1497 | HistoryEventList_ms6 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1498 | HistoryEventList_ID7 | U16 |  |  |  |  | R | The 7th most recent historical event ID
| 1499 | HistoryEventList_yM7 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 149A | HistoryEventList_dH7 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 149B | HistoryEventList_ms7 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 149C | HistoryEventList_ID8 | U16 |  |  |  |  | R | The 8th most recent historical event ID
| 149D | HistoryEventList_yM8 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 149E | HistoryEventList_dH8 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 149F | HistoryEventList_ms8 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14A0 | HistoryEventList_ID9 | U16 |  |  |  |  | R | The 9th most recent historical event ID
| 14A1 | HistoryEventList_yM9 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14A2 | HistoryEventList_dH9 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14A3 | HistoryEventList_ms9 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14A4 | HistoryEventList_ID10 | U16 |  |  |  |  | R | The 10th most recent historical event ID
| 14A5 | HistoryEventList_yM10 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14A6 | HistoryEventList_dH10 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14A7 | HistoryEventList_ms10 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14A8 | HistoryEventList_ID11 | U16 |  |  |  |  | R | The 11th most recent historical event ID
| 14A9 | HistoryEventList_yM11 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14AA | HistoryEventList_dH11 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14AB | HistoryEventList_ms11 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14AC | HistoryEventList_ID12 | U16 |  |  |  |  | R | The 12th most recent historical event ID
| 14AD | HistoryEventList_yM12 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14AE | HistoryEventList_dH12 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14AF | HistoryEventList_ms12 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14B0 | HistoryEventList_ID13 | U16 |  |  |  |  | R | The 13th most recent historical event ID
| 14B1 | HistoryEventList_yM13 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14B2 | HistoryEventList_dH13 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14B3 | HistoryEventList_ms13 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14B4 | HistoryEventList_ID14 | U16 |  |  |  |  | R | The 14th most recent historical event ID
| 14B5 | HistoryEventList_yM14 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14B6 | HistoryEventList_dH14 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14B7 | HistoryEventList_ms14 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14B8 | HistoryEventList_ID15 | U16 |  |  |  |  | R | The 15th most recent historical event ID
| 14B9 | HistoryEventList_yM15 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14BA | HistoryEventList_dH15 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14BB | HistoryEventList_ms15 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14BC | HistoryEventList_ID16 | U16 |  |  |  |  | R | The 16th most recent historical event ID
| 14BD | HistoryEventList_yM16 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14BE | HistoryEventList_dH16 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14BF | HistoryEventList_ms16 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14C0 | HistoryEventList_ID17 | U16 |  |  |  |  | R | The 17th most recent historical event ID
| 14C1 | HistoryEventList_yM17 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14C2 | HistoryEventList_dH17 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14C3 | HistoryEventList_ms17 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14C4 | HistoryEventList_ID18 | U16 |  |  |  |  | R | The 18th most recent historical event ID
| 14C5 | HistoryEventList_yM18 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14C6 | HistoryEventList_dH18 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14C7 | HistoryEventList_ms18 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14C8 | HistoryEventList_ID19 | U16 |  |  |  |  | R | The 19th most recent historical event ID
| 14C9 | HistoryEventList_yM19 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14CA | HistoryEventList_dH19 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14CB | HistoryEventList_ms19 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14CC | HistoryEventList_ID20 | U16 |  |  |  |  | R | The 20th most recent historical event ID
| 14CD | HistoryEventList_yM20 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14CE | HistoryEventList_dH20 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14CF | HistoryEventList_ms20 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14D0 | HistoryEventList_ID21 | U16 |  |  |  |  | R | The 21th most recent historical event ID
| 14D1 | HistoryEventList_yM21 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14D2 | HistoryEventList_dH21 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14D3 | HistoryEventList_ms21 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14D4 | HistoryEventList_ID22 | U16 |  |  |  |  | R | The 22th most recent historical event ID
| 14D5 | HistoryEventList_yM22 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14D6 | HistoryEventList_dH22 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14D7 | HistoryEventList_ms22 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14D8 | HistoryEventList_ID23 | U16 |  |  |  |  | R | The 23th most recent historical event ID
| 14D9 | HistoryEventList_yM23 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14DA | HistoryEventList_dH23 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14DB | HistoryEventList_ms23 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14DC | HistoryEventList_ID24 | U16 |  |  |  |  | R | The 24th most recent historical event ID
| 14DD | HistoryEventList_yM24 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14DE | HistoryEventList_dH24 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14DF | HistoryEventList_ms24 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14E0 | HistoryEventList_ID25 | U16 |  |  |  |  | R | The 25th most recent historical event ID
| 14E1 | HistoryEventList_yM25 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14E2 | HistoryEventList_dH25 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14E3 | HistoryEventList_ms25 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14E4 | HistoryEventList_ID26 | U16 |  |  |  |  | R | The 26th most recent historical event ID
| 14E5 | HistoryEventList_yM26 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14E6 | HistoryEventList_dH26 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14E7 | HistoryEventList_ms26 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14E8 | HistoryEventList_ID27 | U16 |  |  |  |  | R | The 27th most recent historical event ID
| 14E9 | HistoryEventList_yM27 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14EA | HistoryEventList_dH27 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14EB | HistoryEventList_ms27 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14EC | HistoryEventList_ID28 | U16 |  |  |  |  | R | The 28th most recent historical event ID
| 14ED | HistoryEventList_yM28 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14EE | HistoryEventList_dH28 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14EF | HistoryEventList_ms28 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14F0 | HistoryEventList_ID29 | U16 |  |  |  |  | R | The 29th most recent historical event ID
| 14F1 | HistoryEventList_yM29 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14F2 | HistoryEventList_dH29 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14F3 | HistoryEventList_ms29 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14F4 | HistoryEventList_ID30 | U16 |  |  |  |  | R | The 30th most recent historical event ID
| 14F5 | HistoryEventList_yM30 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14F6 | HistoryEventList_dH30 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14F7 | HistoryEventList_ms30 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14F8 | HistoryEventList_ID31 | U16 |  |  |  |  | R | The 31th most recent historical event ID
| 14F9 | HistoryEventList_yM31 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14FA | HistoryEventList_dH31 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14FB | HistoryEventList_ms31 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14FC | HistoryEventList_ID32 | U16 |  |  |  |  | R | The 32th most recent historical event ID
| 14FD | HistoryEventList_yM32 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14FE | HistoryEventList_dH32 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14FF | HistoryEventList_ms32 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1500 | HistoryEventList_ID33 | U16 |  |  |  |  | R | The 33th most recent historical event ID
| 1501 | HistoryEventList_yM33 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1502 | HistoryEventList_dH33 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1503 | HistoryEventList_ms33 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1504 | HistoryEventList_ID34 | U16 |  |  |  |  | R | The 34th most recent historical event ID
| 1505 | HistoryEventList_yM34 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1506 | HistoryEventList_dH34 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1507 | HistoryEventList_ms34 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1508 | HistoryEventList_ID35 | U16 |  |  |  |  | R | The 35th most recent historical event ID
| 1509 | HistoryEventList_yM35 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 150A | HistoryEventList_dH35 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 150B | HistoryEventList_ms35 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 150C | HistoryEventList_ID36 | U16 |  |  |  |  | R | The 36th most recent historical event ID
| 150D | HistoryEventList_yM36 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 150E | HistoryEventList_dH36 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 150F | HistoryEventList_ms36 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1510 | HistoryEventList_ID37 | U16 |  |  |  |  | R | The 37th most recent historical event ID
| 1511 | HistoryEventList_yM37 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1512 | HistoryEventList_dH37 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1513 | HistoryEventList_ms37 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1514 | HistoryEventList_ID38 | U16 |  |  |  |  | R | The 38th most recent historical event ID
| 1515 | HistoryEventList_yM38 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1516 | HistoryEventList_dH38 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1517 | HistoryEventList_ms38 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1518 | HistoryEventList_ID39 | U16 |  |  |  |  | R | The 39th most recent historical event ID
| 1519 | HistoryEventList_yM39 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 151A | HistoryEventList_dH39 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 151B | HistoryEventList_ms39 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 151C | HistoryEventList_ID40 | U16 |  |  |  |  | R | The 40th most recent historical event ID
| 151D | HistoryEventList_yM40 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 151E | HistoryEventList_dH40 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 151F | HistoryEventList_ms40 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1520 | HistoryEventList_ID41 | U16 |  |  |  |  | R | The 41th most recent historical event ID
| 1521 | HistoryEventList_yM41 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1522 | HistoryEventList_dH41 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1523 | HistoryEventList_ms41 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1524 | HistoryEventList_ID42 | U16 |  |  |  |  | R | The 42th most recent historical event ID
| 1525 | HistoryEventList_yM42 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1526 | HistoryEventList_dH42 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1527 | HistoryEventList_ms42 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1528 | HistoryEventList_ID43 | U16 |  |  |  |  | R | The 43th most recent historical event ID
| 1529 | HistoryEventList_yM43 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 152A | HistoryEventList_dH43 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 152B | HistoryEventList_ms43 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 152C | HistoryEventList_ID44 | U16 |  |  |  |  | R | The 44th most recent historical event ID
| 152D | HistoryEventList_yM44 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 152E | HistoryEventList_dH44 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 152F | HistoryEventList_ms44 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1530 | HistoryEventList_ID45 | U16 |  |  |  |  | R | The 45th most recent historical event ID
| 1531 | HistoryEventList_yM45 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1532 | HistoryEventList_dH45 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1533 | HistoryEventList_ms45 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1534 | HistoryEventList_ID46 | U16 |  |  |  |  | R | The 46th most recent historical event ID
| 1535 | HistoryEventList_yM46 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1536 | HistoryEventList_dH46 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1537 | HistoryEventList_ms46 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1538 | HistoryEventList_ID47 | U16 |  |  |  |  | R | The 47th most recent historical event ID
| 1539 | HistoryEventList_yM47 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 153A | HistoryEventList_dH47 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 153B | HistoryEventList_ms47 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 153C | HistoryEventList_ID48 | U16 |  |  |  |  | R | The 48th most recent historical event ID
| 153D | HistoryEventList_yM48 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 153E | HistoryEventList_dH48 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 153F | HistoryEventList_ms48 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1540 | HistoryEventList_ID49 | U16 |  |  |  |  | R | The 49th most recent historical event ID
| 1541 | HistoryEventList_yM49 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1542 | HistoryEventList_dH49 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1543 | HistoryEventList_ms49 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1544 | HistoryEventList_ID50 | U16 |  |  |  |  | R | The 50th most recent historical event ID
| 1545 | HistoryEventList_yM50 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1546 | HistoryEventList_dH50 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1547 | HistoryEventList_ms50 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1548 | HistoryEventList_ID51 | U16 |  |  |  |  | R | The 51th most recent historical event ID
| 1549 | HistoryEventList_yM51 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 154A | HistoryEventList_dH51 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 154B | HistoryEventList_ms51 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 154C | HistoryEventList_ID52 | U16 |  |  |  |  | R | The 52th most recent historical event ID
| 154D | HistoryEventList_yM52 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 154E | HistoryEventList_dH52 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 154F | HistoryEventList_ms52 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1550 | HistoryEventList_ID53 | U16 |  |  |  |  | R | The 53th most recent historical event ID
| 1551 | HistoryEventList_yM53 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1552 | HistoryEventList_dH53 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1553 | HistoryEventList_ms53 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1554 | HistoryEventList_ID54 | U16 |  |  |  |  | R | The 54th most recent historical event ID
| 1555 | HistoryEventList_yM54 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1556 | HistoryEventList_dH54 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1557 | HistoryEventList_ms54 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1558 | HistoryEventList_ID55 | U16 |  |  |  |  | R | The 55th most recent historical event ID
| 1559 | HistoryEventList_yM55 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 155A | HistoryEventList_dH55 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 155B | HistoryEventList_ms55 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 155C | HistoryEventList_ID56 | U16 |  |  |  |  | R | The 56th most recent historical event ID
| 155D | HistoryEventList_yM56 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 155E | HistoryEventList_dH56 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 155F | HistoryEventList_ms56 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1560 | HistoryEventList_ID57 | U16 |  |  |  |  | R | The 57th most recent historical event ID
| 1561 | HistoryEventList_yM57 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1562 | HistoryEventList_dH57 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1563 | HistoryEventList_ms57 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1564 | HistoryEventList_ID58 | U16 |  |  |  |  | R | The 58th most recent historical event ID
| 1565 | HistoryEventList_yM58 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1566 | HistoryEventList_dH58 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1567 | HistoryEventList_ms58 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1568 | HistoryEventList_ID59 | U16 |  |  |  |  | R | The 59th most recent historical event ID
| 1569 | HistoryEventList_yM59 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 156A | HistoryEventList_dH59 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 156B | HistoryEventList_ms59 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 156C | HistoryEventList_ID60 | U16 |  |  |  |  | R | The 60th most recent historical event ID
| 156D | HistoryEventList_yM60 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 156E | HistoryEventList_dH60 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 156F | HistoryEventList_ms60 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1570 | HistoryEventList_ID61 | U16 |  |  |  |  | R | The 61th most recent historical event ID
| 1571 | HistoryEventList_yM61 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1572 | HistoryEventList_dH61 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1573 | HistoryEventList_ms61 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1574 | HistoryEventList_ID62 | U16 |  |  |  |  | R | The 62th most recent historical event ID
| 1575 | HistoryEventList_yM62 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1576 | HistoryEventList_dH62 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1577 | HistoryEventList_ms62 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1578 | HistoryEventList_ID63 | U16 |  |  |  |  | R | The 63th most recent historical event ID
| 1579 | HistoryEventList_yM63 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 157A | HistoryEventList_dH63 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 157B | HistoryEventList_ms63 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 157C | HistoryEventList_ID64 | U16 |  |  |  |  | R | The 64th most recent historical event ID
| 157D | HistoryEventList_yM64 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 157E | HistoryEventList_dH64 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 157F | HistoryEventList_ms64 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1580 | HistoryEventList_ID65 | U16 |  |  |  |  | R | The 65th most recent historical event ID
| 1581 | HistoryEventList_yM65 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1582 | HistoryEventList_dH65 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1583 | HistoryEventList_ms65 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1584 | HistoryEventList_ID66 | U16 |  |  |  |  | R | The 66th most recent historical event ID
| 1585 | HistoryEventList_yM66 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1586 | HistoryEventList_dH66 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1587 | HistoryEventList_ms66 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1588 | HistoryEventList_ID67 | U16 |  |  |  |  | R | The 67th most recent historical event ID
| 1589 | HistoryEventList_yM67 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 158A | HistoryEventList_dH67 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 158B | HistoryEventList_ms67 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 158C | HistoryEventList_ID68 | U16 |  |  |  |  | R | The 68th most recent historical event ID
| 158D | HistoryEventList_yM68 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 158E | HistoryEventList_dH68 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 158F | HistoryEventList_ms68 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1590 | HistoryEventList_ID69 | U16 |  |  |  |  | R | The 69th most recent historical event ID
| 1591 | HistoryEventList_yM69 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1592 | HistoryEventList_dH69 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1593 | HistoryEventList_ms69 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1594 | HistoryEventList_ID70 | U16 |  |  |  |  | R | The 70th most recent historical event ID
| 1595 | HistoryEventList_yM70 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1596 | HistoryEventList_dH70 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1597 | HistoryEventList_ms70 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1598 | HistoryEventList_ID71 | U16 |  |  |  |  | R | The 71th most recent historical event ID
| 1599 | HistoryEventList_yM71 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 159A | HistoryEventList_dH71 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 159B | HistoryEventList_ms71 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 159C | HistoryEventList_ID72 | U16 |  |  |  |  | R | The 72th most recent historical event ID
| 159D | HistoryEventList_yM72 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 159E | HistoryEventList_dH72 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 159F | HistoryEventList_ms72 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15A0 | HistoryEventList_ID73 | U16 |  |  |  |  | R | The 73th most recent historical event ID
| 15A1 | HistoryEventList_yM73 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15A2 | HistoryEventList_dH73 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15A3 | HistoryEventList_ms73 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15A4 | HistoryEventList_ID74 | U16 |  |  |  |  | R | The 74th most recent historical event ID
| 15A5 | HistoryEventList_yM74 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15A6 | HistoryEventList_dH74 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15A7 | HistoryEventList_ms74 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15A8 | HistoryEventList_ID75 | U16 |  |  |  |  | R | The 75th most recent historical event ID
| 15A9 | HistoryEventList_yM75 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15AA | HistoryEventList_dH75 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15AB | HistoryEventList_ms75 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15AC | HistoryEventList_ID76 | U16 |  |  |  |  | R | The 76th most recent historical event ID
| 15AD | HistoryEventList_yM76 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15AE | HistoryEventList_dH76 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15AF | HistoryEventList_ms76 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15B0 | HistoryEventList_ID77 | U16 |  |  |  |  | R | The 77th most recent historical event ID
| 15B1 | HistoryEventList_yM77 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15B2 | HistoryEventList_dH77 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15B3 | HistoryEventList_ms77 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15B4 | HistoryEventList_ID78 | U16 |  |  |  |  | R | The 78th most recent historical event ID
| 15B5 | HistoryEventList_yM78 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15B6 | HistoryEventList_dH78 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15B7 | HistoryEventList_ms78 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15B8 | HistoryEventList_ID79 | U16 |  |  |  |  | R | The 79th most recent historical event ID
| 15B9 | HistoryEventList_yM79 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15BA | HistoryEventList_dH79 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15BB | HistoryEventList_ms79 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15BC | HistoryEventList_ID80 | U16 |  |  |  |  | R | The 80th most recent historical event ID
| 15BD | HistoryEventList_yM80 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15BE | HistoryEventList_dH80 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15BF | HistoryEventList_ms80 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15C0 | HistoryEventList_ID81 | U16 |  |  |  |  | R | The 81th most recent historical event ID
| 15C1 | HistoryEventList_yM81 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15C2 | HistoryEventList_dH81 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15C3 | HistoryEventList_ms81 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15C4 | HistoryEventList_ID82 | U16 |  |  |  |  | R | The 82th most recent historical event ID
| 15C5 | HistoryEventList_yM82 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15C6 | HistoryEventList_dH82 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15C7 | HistoryEventList_ms82 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15C8 | HistoryEventList_ID83 | U16 |  |  |  |  | R | The 83th most recent historical event ID
| 15C9 | HistoryEventList_yM83 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15CA | HistoryEventList_dH83 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15CB | HistoryEventList_ms83 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15CC | HistoryEventList_ID84 | U16 |  |  |  |  | R | The 84th most recent historical event ID
| 15CD | HistoryEventList_yM84 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15CE | HistoryEventList_dH84 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15CF | HistoryEventList_ms84 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15D0 | HistoryEventList_ID85 | U16 |  |  |  |  | R | The 85th most recent historical event ID
| 15D1 | HistoryEventList_yM85 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15D2 | HistoryEventList_dH85 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15D3 | HistoryEventList_ms85 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15D4 | HistoryEventList_ID86 | U16 |  |  |  |  | R | The 86th most recent historical event ID
| 15D5 | HistoryEventList_yM86 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15D6 | HistoryEventList_dH86 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15D7 | HistoryEventList_ms86 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15D8 | HistoryEventList_ID87 | U16 |  |  |  |  | R | The 87th most recent historical event ID
| 15D9 | HistoryEventList_yM87 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15DA | HistoryEventList_dH87 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15DB | HistoryEventList_ms87 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15DC | HistoryEventList_ID88 | U16 |  |  |  |  | R | The 88th most recent historical event ID
| 15DD | HistoryEventList_yM88 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15DE | HistoryEventList_dH88 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15DF | HistoryEventList_ms88 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15E0 | HistoryEventList_ID89 | U16 |  |  |  |  | R | The 89th most recent historical event ID
| 15E1 | HistoryEventList_yM89 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15E2 | HistoryEventList_dH89 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15E3 | HistoryEventList_ms89 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15E4 | HistoryEventList_ID90 | U16 |  |  |  |  | R | The 90th most recent historical event ID
| 15E5 | HistoryEventList_yM90 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15E6 | HistoryEventList_dH90 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15E7 | HistoryEventList_ms90 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15E8 | HistoryEventList_ID91 | U16 |  |  |  |  | R | The 91th most recent historical event ID
| 15E9 | HistoryEventList_yM91 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15EA | HistoryEventList_dH91 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15EB | HistoryEventList_ms91 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15EC | HistoryEventList_ID92 | U16 |  |  |  |  | R | The 92th most recent historical event ID
| 15ED | HistoryEventList_yM92 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15EE | HistoryEventList_dH92 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15EF | HistoryEventList_ms92 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15F0 | HistoryEventList_ID93 | U16 |  |  |  |  | R | The 93th most recent historical event ID
| 15F1 | HistoryEventList_yM93 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15F2 | HistoryEventList_dH93 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15F3 | HistoryEventList_ms93 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15F4 | HistoryEventList_ID94 | U16 |  |  |  |  | R | The 94th most recent historical event ID
| 15F5 | HistoryEventList_yM94 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15F6 | HistoryEventList_dH94 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15F7 | HistoryEventList_ms94 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15F8 | HistoryEventList_ID95 | U16 |  |  |  |  | R | The 95th most recent historical event ID
| 15F9 | HistoryEventList_yM95 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15FA | HistoryEventList_dH95 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15FB | HistoryEventList_ms95 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15FC | HistoryEventList_ID96 | U16 |  |  |  |  | R | The 96th most recent historical event ID
| 15FD | HistoryEventList_yM96 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15FE | HistoryEventList_dH96 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15FF | HistoryEventList_ms96 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1600 | HistoryEventList_ID97 | U16 |  |  |  |  | R | The 97th most recent historical event ID
| 1601 | HistoryEventList_yM97 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1602 | HistoryEventList_dH97 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1603 | HistoryEventList_ms97 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1604 | HistoryEventList_ID98 | U16 |  |  |  |  | R | The 98th most recent historical event ID
| 1605 | HistoryEventList_yM98 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1606 | HistoryEventList_dH98 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1607 | HistoryEventList_ms98 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1608 | HistoryEventList_ID99 | U16 |  |  |  |  | R | The 99th most recent historical event ID
| 1609 | HistoryEventList_yM99 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 160A | HistoryEventList_dH99 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 160B | HistoryEventList_ms99 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 160C | HistoryEventList_ID100 | U16 |  |  |  |  | R | The 100th most recent historical event ID
| 160D | HistoryEventList_yM100 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 160E | HistoryEventList_dH100 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 160F | HistoryEventList_ms100 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1610 | EnergyStatistics1 | U32 | 0.01 | kWh |  |  | R | Article 1 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1611
| 1612 | EnergyStatistics2 | U32 | 0.01 | kWh |  |  | R | Article 2 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1613
| 1614 | EnergyStatistics3 | U32 | 0.01 | kWh |  |  | R | Article 3 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1615
| 1616 | EnergyStatistics4 | U32 | 0.01 | kWh |  |  | R | Article 4 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1617
| 1618 | EnergyStatistics5 | U32 | 0.01 | kWh |  |  | R | Article 5 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1619
| 161A | EnergyStatistics6 | U32 | 0.01 | kWh |  |  | R | Article 6 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
161B
| 161C | EnergyStatistics7 | U32 | 0.01 | kWh |  |  | R | Article 7 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
161D
| 161E | EnergyStatistics8 | U32 | 0.01 | kWh |  |  | R | Article 8 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
161F
| 1620 | EnergyStatistics9 | U32 | 0.01 | kWh |  |  | R | Article 9 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1621
| 1622 | EnergyStatistics10 | U32 | 0.01 | kWh |  |  | R | Article 10 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1623
| 1624 | EnergyStatistics11 | U32 | 0.01 | kWh |  |  | R | Article 11 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1625
| 1626 | EnergyStatistics12 | U32 | 0.01 | kWh |  |  | R | Article 12 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1627
| 1628 | EnergyStatistics13 | U32 | 0.01 | kWh |  |  | R | Article 13 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1629
| 162A | EnergyStatistics14 | U32 | 0.01 | kWh |  |  | R | Article 14 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
162B
| 162C | EnergyStatistics15 | U32 | 0.01 | kWh |  |  | R | Article 15 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
162D
| 162E | EnergyStatistics16 | U32 | 0.01 | kWh |  |  | R | Article 16 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
162F
| 1630 | EnergyStatistics17 | U32 | 0.01 | kWh |  |  | R | Article 17 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1631
| 1632 | EnergyStatistics18 | U32 | 0.01 | kWh |  |  | R | Article 18 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1633
| 1634 | EnergyStatistics19 | U32 | 0.01 | kWh |  |  | R | Article 19 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1635
| 1636 | EnergyStatistics20 | U32 | 0.01 | kWh |  |  | R | Article 20 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1637
| 1638 | EnergyStatistics21 | U32 | 0.01 | kWh |  |  | R | Article 21 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1639
| 163A | EnergyStatistics22 | U32 | 0.01 | kWh |  |  | R | Article 22 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
163B
| 163C | EnergyStatistics23 | U32 | 0.01 | kWh |  |  | R | Article 23 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
163D
| 163E | EnergyStatistics24 | U32 | 0.01 | kWh |  |  | R | Article 24 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
163F
| 1640 | EnergyStatistics25 | U32 | 0.01 | kWh |  |  | R | Article 25 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1641
| 1642 | EnergyStatistics26 | U32 | 0.01 | kWh |  |  | R | Article 26 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1643
| 1644 | EnergyStatistics27 | U32 | 0.01 | kWh |  |  | R | Article 27 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1645
| 1646 | EnergyStatistics28 | U32 | 0.01 | kWh |  |  | R | Article 28 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1647
| 1648 | EnergyStatistics29 | U32 | 0.01 | kWh |  |  | R | Article 29 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1649
| 164A | EnergyStatistics30 | U32 | 0.01 | kWh |  |  | R | Article 30 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
164B
| 164C | EnergyStatistics31 | U32 | 0.01 | kWh |  |  | R | Article 31 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
164D
| 164E | EnergyStatistics32 | U32 | 0.01 | kWh |  |  | R | Article 32 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
164F
| 1650 | EnergyStatistics33 | U32 | 0.01 | kWh |  |  | R | Article 33 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1651
| 1652 | EnergyStatistics34 | U32 | 0.01 | kWh |  |  | R | Article 34 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1653
| 1654 | EnergyStatistics35 | U32 | 0.01 | kWh |  |  | R | Article 35 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1655
| 1656 | EnergyStatistics36 | U32 | 0.01 | kWh |  |  | R | Article 36 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1657
| 1658 | EnergyStatistics37 | U32 | 0.01 | kWh |  |  | R | Article 37 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1659
| 165A | EnergyStatistics38 | U32 | 0.01 | kWh |  |  | R | Article 38 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
165B
| 165C | EnergyStatistics39 | U32 | 0.01 | kWh |  |  | R | Article 39 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
165D
| 165E | EnergyStatistics40 | U32 | 0.01 | kWh |  |  | R | Article 40 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
165F
Core function configuration (0x2000-0x207F)
| 2000 | AddressMask_Config_Core1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid.
2001
2002
2003
| 2004 | Country_Code | U16 |  |  |  |  | RW | Safety country, used for storage
| 2005 | Safety_Version | U16 |  |  |  |  | RW | The version number of the safety parameters of the communication host (upper computer).
| 2006 | Factory_Reset | U16 |  |  | 1 | 255 | RW | Restore factory registers; The bit value is 1 valid. Bit0: Clear battery Bit1: Clear event record Bit2: Restore default values ​​for all function configuration parameters When reading, return the status of the last write operation: 0x0000: success 0x0001-0x00FF: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong
| 2007 | Safety_Name1 | ASCII |  |  |  |  | RW | The first and second place in the name of the safety-regulated country. The upper 8 bits of the register store the first digit of the safety name; The lower 8 bits of the register store the second bit of the safety name.
| 2008 | Safety_Name2 | ASCII |  |  |  |  | RW | The third and fourth place in the name of the safety-regulated country. The upper 8 bits of the register store the third digit of the safety name; The lower 8 bits of the register store the 4th bit of the safety name.
| 2009 | Safety_Name3 | ASCII |  |  |  |  | RW | The 5th and 6th place in the name of the safety-regulated country. The upper 8 bits of the register store the 5th digit of the safety name; The lower 8 bits of the register store the 6th bit of the safety name.
| 200A | Safety_Name4 | ASCII |  |  |  |  | RW | The 7th and 8th place in the name of the safety-regulated country. The upper 8 bits of the register store the 7th bit of the safety name; The lower 8 bits of the register store the 8th bit of the safety name.
| 200B | Safety_Name5 | ASCII |  |  |  |  | RW | The ninth and tenth place in the name of safety regulations. The upper 8 bits of the register store the 9th bit of the safety name; The lower 8 bits of the register store the 10th bit of the safety name.
200C
200D
200E
200F
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
201A
201B
201C
201D
201E
201F
2020
2021
2022
2023
2024
2025
2026
2027
2028
2029
202A
202B
202C
202D
202E
202F
2030
2031
2032
2033
2034
2035
2036
2037
2038
| 2039 | Upgrade_Total | U16 |  |  |  |  | R | Total number of upgrade targets. When upgrading one or more targets simultaneously using the same firmware, the value of this register indicates the total number of upgrade targets.
| 203A | Upgrade_Result_Table1 | U16 |  |  |  |  | R | Upgrade result bit table 1. A bit value of 0 indicates an incomplete or failed upgrade. A bit value of 1 indicates a successful upgrade. The lowest bit indicates the upgrade target numbered 1. The highest bit indicates the upgrade target numbered 16.
| 203B | Upgrade_Result_Table2 | U16 |  |  |  |  | R | Upgrade result bit table 2. A bit value of 0 indicates an incomplete or failed upgrade. A bit value of 1 indicates a successful upgrade. The lowest bit indicates the upgrade target numbered 17. The highest bit indicates the upgrade target numbered 32.
| 203C | Remote_Download_Control | U16 |  |  |  |  | W | Remote Download Control Register. (Only single target operation is supported) High byte. Writing to 0xA5 is valid. The low byte contains the combination of chips to be upgraded, and each bit is explained as follows. Bit0: Communication board. Bit1: control board 1 (primary DSP). Bit2: control board 2 (sub-DSP). Bit3: Fuse. Bit4: BMS. Bit5: PCU; Bit5: PCU. Bit6: BDU;
| 203D | Remote_Upgrade_Control | U16 |  |  |  |  | W | Remote upgrade control register. High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded, and the explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (secondary DSP); Bit3: Fuse Bit4：BMS； Bit5：PCU； Bit6：BDU；
| 203E | Local_Upgrade_Control | U16 |  |  |  |  | W | High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded, and the explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (secondary DSP); Bit3: Fuse Bit4：BMS； Bit5：PCU； Bit6：BDU；
| 203F | Local_Upgrade_Status | U16 |  |  |  |  | R | Current upgrade progress The high byte indicates the current target chip to be upgraded: 0x00: Not in the upgrade state; 0x01: Main DSP upgrade; 0x02: Secondary DSP upgrade; 0x03: ARM upgrade; 0x04: FUSE upgrade; 0x05：BMS upgrade； 0x06：PCU upgrade； 0x07：BDU upgrade； The low byte indicates the current upgrade progress: The progress range is 0-100%
PCU&BDU数据区(0x6000-0x6FFF)
| 6000 | AddressMask_PCU1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of this field plus 1 is located. 0 means invalid; 1 means valid.
6001
6002
6003
| 6004 | PCU_Number | [5 empty] | R | Total number of PCUs online.
| 6005 | [6 empty] | R | Aggregate Information Reservation
| 6006 | [6 empty] | R | Aggregate Information Reservation
| 6007 | [6 empty] | R | Aggregate Information Reservation
| 6008 | [6 empty] | R | Aggregate Information Reservation
| 6009 | [6 empty] | R | Aggregate Information Reservation
| 600A | [6 empty] | R | Aggregate Information Reservation
| 600B | [6 empty] | R | Aggregate Information Reservation
| 600C | [6 empty] | R | Aggregate Information Reservation
| 600D | [6 empty] | R | Aggregate Information Reservation
| 600E | [6 empty] | R | Aggregate Information Reservation
| 600F | [6 empty] | R | Aggregate Information Reservation
| 6010 | PCU_ID | U16 |  |  |  |  | R | PCU number. Numbering starts from 1.
| 6011 | PCU_SN0 | ASCII |  |  |  |  | R | PCU serial number 0
| 6012 | PCU_SN1 | ASCII |  |  |  |  | R | PCU serial number 1
| 6013 | PCU_SN2 | ASCII |  |  |  |  | R | PCU serial number 2
| 6014 | PCU_SN3 | ASCII |  |  |  |  | R | PCU serial number 3
| 6015 | PCU_SN4 | ASCII |  |  |  |  | R | PCU serial number 4
| 6016 | PCU_SN5 | ASCII |  |  |  |  | R | PCU serial number 5
| 6017 | PCU_SN6 | ASCII |  |  |  |  | R | PCU serial number 6
| 6018 | PCU_SN7 | ASCII |  |  |  |  | R | PCU serial number 7
| 6019 | PCU_SN8 | ASCII |  |  |  |  | R | PCU serial number 8
| 601A | PCU_SN9 | ASCII |  |  |  |  | R | PCU serial number 9
| 601B | PCU_Software_Version1 | ASCII |  |  |  |  | R | Software version number 1
| 601C | PCU_Software_Version2 | ASCII |  |  |  |  | R | Software version number 2
| 601D | PCU_Hardware_Version | U16 |  |  |  |  | R | Hardware Version Number
| 601E | PCU_Can1_Version | U16 |  |  |  |  | R | CAN1 protocol version number
| 601F | PCU_Can2_Version | U16 |  |  |  |  | R | CAN2 protocol version number
| 6020 | PCU_Work_State | U16 |  |  |  |  | R | Module Status 0：Wait to upgrade 1: Check 2：Normal 3: Battery Activated 4: Fault 5：Permanent Fault
| 6021 | PCU_Internal_Temperature | U16 | 1 | ℃ |  |  | R | Chassis internal temperature
| 6022 | PCU_Radiator_Temperature1 | I16 | 1 | ℃ |  |  | R | Heatsink 1 temperature
| 6023 | PCU_Radiator_Temperature2 | I16 | 1 | ℃ |  |  | R | Heatsink 2 temperature
| 6024 | PCU_Warning1 | U16 |  |  |  |  | R | Warning 1
| 6025 | PCU_Warning2 | U16 |  |  |  |  | R | Warning 2
| 6026 | PCU_Warning3 | U16 |  |  |  |  | R | Warning 3
| 6027 | PCU_Warning4 | U16 |  |  |  |  | R | Warning 4
| 6028 | PCU_Fault1 | U16 |  |  |  |  | R | Fault 1
| 6029 | PCU_Fault2 | U16 |  |  |  |  | R | Fault 2
| 602A | PCU_Fault3 | U16 |  |  |  |  | R | Fault 3
| 602B | PCU_Fault4 | U16 |  |  |  |  | R | Fault 4
| 602C | PCU_DC_High_Voltage | U16 | 0.1 | V | 0 |  | R | DC high voltage side voltage
| 602D | PCU_DC_Low_Voltage | U16 | 0.1 | V | 0 |  | R | DC low voltage side voltage
| 602E | PCU_Low_Current | I16 | 0.1 | A |  |  | R | DC low voltage side current
| 602F | PCU_Low_Power | I16 | 0.01 | kW |  |  | R | DC low voltage side power
| 6030 | PCU_BusP | U16 | 0.1 | V |  |  | R | Positive bus voltage
| 6031 | PCU_BusN | U16 | 0.1 | V |  |  | R | Negative bus voltage
| 6032 | PCU_FC_Voltage1 | U16 | 0.1 | V |  |  | R | Fly Across Capacitor Voltage 1
| 6033 | PCU_FC_Voltage2 | U16 | 0.1 | V |  |  | R | Fly across capacitor voltage 2
| 6034 | PCU_FC_Voltage3 | U16 | 0.1 | V |  |  | R | Fly across capacitor voltage 3
| 6035 | PCU_FC_Voltage4 | U16 | 0.1 | V |  |  | R | Fly across capacitor voltage 4
| 6036 | PCU_IL_Current1 | I16 | 0.1 | A |  |  | R | Inductive current branch 1
| 6037 | PCU_IL_Current2 | I16 | 0.1 | A |  |  | R | Inductive current branch 2
| 6038 | PCU_IL_Current3 | I16 | 0.1 | A |  |  | R | Inductive current branch 3
| 6039 | PCU_IL_Current4 | I16 | 0.1 | A |  |  | R | Inductive current branch 4
| 603A | [6 empty] | R
| 603B | [6 empty] | R
| 603C | [6 empty] | R
| 603D | [6 empty] | R
| 603E | [6 empty] | R
| 603F | [6 empty] | R
| 6040 | AddressMask_PCU2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of this field plus 1 is located. 0 means invalid; 1 means valid.
6041
6042
6043
| 6044 | PCU_Inquire | U16 |  |  | 1 | 32 | RW | PCU Query Control Word. Select the PCU module to be read or set by setting this register.
| 6045 | PCU_Remote_On_Off | U16 |  |  | 0 | 3 | RW | DC Module Remote On/Off 0: Shutdown 1: Disable charging 2: Discharge prohibited 3: Allow charging and discharging
| 6046 | PCU_Max_Charge_Current | U16 | 0.1 | A | 0 | 65535 | RW | Max. charging current of DC module
| 6047 | PCU_Max_Discharge_Current | U16 | 0.1 | A | 0 | 65535 | RW | Max. discharge current of DC module
6048
6049
604A
604B
604C
604D
604E
604F
6050
6051
6052
6053
6054
6055
6056
6057
6058
6059
605A
605B
605C
605D
605E
605F
6060
6061
6062
6063
6064
6065
6066
6067
6068
6069
606A
606B
606C
606D
606E
606F
6070
6071
6072
6073
6074
6075
6076
6077
6078
6079
607A
607B
607C
607D
607E
607F
| 6080 | AddressMask_BDU1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of this field plus 1 is located. 0 means invalid; 1 means valid.
6081
6082
6083
| 6084 | BDU_Number | U16 |  |  |  |  | R | Total number of BDUs online.
| 6085 | [6 empty] | R | Aggregate Information Reservation
| 6086 | [6 empty] | R | Aggregate Information Reservation
| 6087 | [6 empty] | R | Aggregate Information Reservation
| 6088 | [6 empty] | R | Aggregate Information Reservation
| 6089 | [6 empty] | R | Aggregate Information Reservation
| 608A | [6 empty] | R | Aggregate Information Reservation
| 608B | [6 empty] | R | Aggregate Information Reservation
| 608C | [6 empty] | R | Aggregate Information Reservation
| 608D | [6 empty] | R | Aggregate Information Reservation
| 608E | [6 empty] | R | Aggregate Information Reservation
| 608F | [6 empty] | R | Aggregate Information Reservation
| 6090 | BDU_ID | U16 |  |  |  |  | R | BDU number. Numbering starts from 1.
| 6091 | BDU_SN0 | ASCII |  |  |  |  | R | BDU serial number 0
| 6092 | BDU_SN1 | ASCII |  |  |  |  | R | BDU serial number 1
| 6093 | BDU_SN2 | ASCII |  |  |  |  | R | BDU serial number 2
| 6094 | BDU_SN3 | ASCII |  |  |  |  | R | BDU serial number 3
| 6095 | BDU_SN4 | ASCII |  |  |  |  | R | BDU serial number 4
| 6096 | BDU_SN5 | ASCII |  |  |  |  | R | BDU Serial Number 5
| 6097 | BDU_SN6 | ASCII |  |  |  |  | R | BDU Serial Number 6
| 6098 | BDU_SN7 | ASCII |  |  |  |  | R | BDU Serial Number 7
| 6099 | BDU_SN8 | ASCII |  |  |  |  | R | BDU serial number 8
| 609A | BDU_SN9 | ASCII |  |  |  |  | R | BDU serial number 9
| 609B | Software_Version_Stage_BDU | ASCII |  |  |  |  | R | BDU chip software version number phase definition bits. The lower 8 bits of the register hold the ASCII code. The default value for the official version is 'V'.
| 609C | Software_Version_Major_BDU | ASCII |  |  |  |  | R | BDU chip software major version number. All chip master version numbers in the same system must be the same, otherwise it is considered as system failure. The high 8 bits of the register store the high digits. The low 8 bits of the register store the low digits.
| 609D | Software_Version_Custom_BDU | ASCII |  |  |  |  | R | BDU chip software non-standard custom version number. Genuine standard software this version number is "00". All chip non-standard custom version number in the same system must be consistent, otherwise it is considered as system failure. The high 8 bits of the register hold the high digits. The low 8 bits of the register store the low digits.
| 609E | Software_Version_Minor_BDU | ASCII |  |  |  |  | R | BDU chip software subversion number. Register high 8 bits to store the high digit. Register low 8 bits hold the low digits.
| 609F | BDU_Fault1 | U16 |  |  |  |  | R | BDU fault information 1
| 60A0 | BDU_Battery_Number | U16 |  |  |  |  | R | Number of single cluster cells
60A1
60A2
60A3
60A4
60A5
60A6
60A7
60A8
60A9
60AA
60AB
60AC
60AD
60AE
60AF
60B0
60B1
60B2
60B3
60B4
60B5
60B6
60B7
60B8
60B9
60BA
60BB
60BC
60BD
60BE
60BF
| 60C0 | AddressMask_BDU2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of this field plus 1 is located. 0 means invalid; 1 means valid.
60C1
60C2
60C3
| 60C4 | BDU_Inquire | U16 |  |  | 1 |  | RW | BDU Query Control Word. Select the BDU module to be read or set by setting this register.
ODM data customization area (0x7000-0x707F)
| 7000 |  | ASCII |  |  |  |  | RW | The address of 0x7000-0x707F is a custom area, which must meet the following format: All registers in this area are in ASCII format. The upper 8 bits of the register store front-end characters and the lower 8 bits store back-end characters. For example, when the character string "1234" is stored in 0x7000, 0x7001, the data in 0x7000 is 0x3132; the data in 0x7001 is 0x3334. Allowed characters include: 0x20-0x7E and 0xFF. 0xFF is automatically ignored during parsing. The string format is defined as follows: Key 1=value 1\r\nkey 2=value 2\r\n The keys supported by this protocol version are: "SN": ODM serial number “machine”：ODM models | End User
BMS（0x9000-0x9FFF）
| 9000 | AddressMask_BMS1_System | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
9001
9002
9003
| 9004 | BMS_Sys_Time | U32 |  |  |  |  | R | BMS system clock Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (starting in 2000)
9005
| 9006 | BMS_CAN_Version | U16 |  |  |  |  | R | CAN protocol version number
| 9007 | BMS_Manufacture_Name0 | U16 |  |  |  |  | R | Manufacturer Information 0
| 9008 | BMS_Manufacture_Name1 | U16 |  |  |  |  | R | Manufacturer Information 1
| 9009 | BMS_Manufacture_Name2 | U16 |  |  |  |  | R | Manufacturer Information 2
| 900A | BMS_Manufacture_Name3 | U16 |  |  |  |  | R | Manufacturer Information 3
| 900B | BMS_Version | U16 |  |  |  |  | R | BMS version number
| 900C | Cell_Type | U16 |  |  |  |  | R | Cell type
| 900D | BaPack_Number | U16 |  |  |  |  | R | High 8 bits: the number of battery packs in parallel Lower 8 bits: the number of battery strings in the battery pack
| 900E | Realtime_Capacity | U16 | 1 | % |  |  | R | Real-time remaining capacity
| 900F | Total_Voltage | U16 | 0.1 | V |  |  | R | Total voltage
| 9010 | Total_Current | U16 | 0.1 | A |  |  | R | Total current
| 9011 | Cell_Average_Temperature | U16 | 0.1 | ℃ |  |  | R | Average cell temperature
| 9012 | SOC | U16 | 1 | % |  |  | R | State of charge
| 9013 | SOH | U16 | 1 | % |  |  | R | Health
| 9014 | BMS_Sys_Protect0 | U16 |  |  |  |  | R | BMS system protection information0
| 9015 | BMS_Sys_Protect1 | U16 |  |  |  |  | R | BMS system protection information 1
| 9016 | BMS_Sys_Alarm0 | U16 |  |  |  |  | R | BMS system alarm information 0
| 9017 | BMS_Sys_Alarm1 | U16 |  |  |  |  | R | BMS system alarm information 1
9018
9019
901A
901B
901C
901D
901E
901F
| 9020 | BMS_Inquire | U16 |  |  |  |  | RW | Battery query control word Bit0-7: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit8-11: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit12-15: The serial number of the fault to be queried, the valid range is 0~5, and 0 means the most recent fault
9021
9022
9023
9024
9025
9026
9027
9028
9029
902A
902B
902C
902D
902E
902F
9030
9031
9032
9033
9034
9035
9036
9037
9038
9039
903A
903B
903C
903D
903E
903F
| 9040 | AddressMask_BMS2_Realtime | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
9041
9042
9043
| 9044 | Pack_RT_ID | U16 |  |  |  |  | R | Real-time data battery pack number. High 8 bits: battery pack serial number Lower 8 bits: battery pack serial number"
| 9045 | Pack_RT_Timestamp | U32 |  |  |  |  | R | Real-time data timestamp
9046
| 9047 | Pack_RT_SN0 | U16 |  |  |  |  | R | Device serial number 0
| 9048 | Pack_RT_SN1 | U16 |  |  |  |  | R | Device serial number 1
| 9049 | Pack_RT_SN2 | U16 |  |  |  |  | R | Device serial number 2
| 904A | Pack_RT_SN3 | U16 |  |  |  |  | R | Device serial number 3
| 904B | Pack_RT_SN4 | U16 |  |  |  |  | R | Device serial number 4
| 904C | Pack_RT_SN5 | U16 |  |  |  |  | R | Device serial number 5
| 904D | Pack_RT_SN6 | U16 |  |  |  |  | R | Device serial number 6
| 904E | Pack_RT_SN7 | U16 |  |  |  |  | R | Device serial number 7
| 904F | Pack_RT_SN8 | U16 |  |  |  |  | R | Device serial number 8
| 9050 | Pack_RT_SN9 | U16 |  |  |  |  | R | Device serial number 9
| 9051 | Pack_RT_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage
| 9052 | Pack_RT_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage
| 9053 | Pack_RT_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage
| 9054 | Pack_RT_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage
| 9055 | Pack_RT_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage
| 9056 | Pack_RT_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage
| 9057 | Pack_RT_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage
| 9058 | Pack_RT_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage
| 9059 | Pack_RT_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage
| 905A | Pack_RT_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 voltage
| 905B | Pack_RT_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 voltage
| 905C | Pack_RT_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 voltage
| 905D | Pack_RT_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 voltage
| 905E | Pack_RT_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 voltage
| 905F | Pack_RT_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 voltage
| 9060 | Pack_RT_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 voltage
| 9061 | Pack_RT_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 voltage
| 9062 | Pack_RT_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage
| 9063 | Pack_RT_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 voltage
| 9064 | Pack_RT_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage
| 9065 | Pack_RT_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 voltage
| 9066 | Pack_RT_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Battery 22 voltage
| 9067 | Pack_RT_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Battery 23 voltage
| 9068 | Pack_RT_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage
| 9069 | Pack_RT_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | The highest voltage of the battery
| 906A | Pack_RT_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum battery voltage
| 906B | Pack_RT_Temperature1_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 1
| 906C | Pack_RT_Temperature2_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 2
| 906D | Pack_RT_Temperature3_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 3
| 906E | Pack_RT_Temperature4_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 4
| 906F | Pack_RT_Temperature_MOS | I16 | 0.1 | ℃ |  |  | R | MOS tube temperature
| 9070 | Pack_RT_Temperature_Env | I16 | 0.1 | ℃ |  |  | R | Ambient temperature in the battery pack
| 9071 | Pack_RT_Current | I16 | 0.1 | A |  |  | R | Battery pack current
| 9072 | Pack_RT_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity
| 9073 | Pack_RT_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | Full charge capacity
| 9074 | Pack_RT_Cycles | U16 | 1 | times |  |  | R | Cycles
| 9075 | Pack_RT_Balance_State | U16 |  |  |  |  | R | Equilibrium
| 9076 | Pack_RT_Alarm_State | U16 |  |  |  |  | R | Alarm status
| 9077 | Pack_RT_Protect_State | U16 |  |  |  |  | R | Protection status
| 9078 | Pack_RT_Fault_State | U16 |  |  |  |  | R | Fault state
| 9079 | Pack_RT_Total_Voltage | U16 | 0.01 | V |  |  | R | Total Voltage
| 907A | Pack_RT_SOC | U16 | 1 | % |  |  | R | SOC
907B
907C
907D
907E
907F
| 9080 | AddressMask_BMS3_Fault | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid
9081
9082
9083
| 9084 | Pack_Fault_ID | U16 |  |  |  |  | R | Real-time faulty battery pack number. Bit0-7: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit8-11: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit12-15: The serial number of the queried fault, the valid range is 0~5, 0 means the most recent fault
| 9085 | Pack_Fault_Timestamp | U32 |  |  |  |  | R | Fault data timestamp
9086
| 9087 | Pack_Fault_SN0 | U16 |  |  |  |  | R | Device serial number 0
| 9088 | Pack_Fault_SN1 | U16 |  |  |  |  | R | Device serial number 1
| 9089 | Pack_Fault_SN2 | U16 |  |  |  |  | R | Device serial number 2
| 908A | Pack_Fault_SN3 | U16 |  |  |  |  | R | Device serial number 3
| 908B | Pack_Fault_SN4 | U16 |  |  |  |  | R | Device serial number 4
| 908C | Pack_Fault_SN5 | U16 |  |  |  |  | R | Device serial number 5
| 908D | Pack_Fault_SN6 | U16 |  |  |  |  | R | Device serial number 6
| 908E | Pack_Fault_SN7 | U16 |  |  |  |  | R | Device serial number 7
| 908F | Pack_Fault_SN8 | U16 |  |  |  |  | R | Device serial number 8
| 9090 | Pack_Fault_SN9 | U16 |  |  |  |  | R | Device serial number 9
| 9091 | Pack_Fault_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage
| 9092 | Pack_Fault_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage
| 9093 | Pack_Fault_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage
| 9094 | Pack_Fault_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage
| 9095 | Pack_Fault_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage
| 9096 | Pack_Fault_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage
| 9097 | Pack_Fault_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage
| 9098 | Pack_Fault_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage
| 9099 | Pack_Fault_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage
| 909A | Pack_Fault_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 voltage
| 909B | Pack_Fault_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 voltage
| 909C | Pack_Fault_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 voltage
| 909D | Pack_Fault_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 voltage
| 909E | Pack_Fault_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 voltage
| 909F | Pack_Fault_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 voltage
| 90A0 | Pack_Fault_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 voltage
| 90A1 | Pack_Fault_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 voltage
| 90A2 | Pack_Fault_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage
| 90A3 | Pack_Fault_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 voltage
| 90A4 | Pack_Fault_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage
| 90A5 | Pack_Fault_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 voltage
| 90A6 | Pack_Fault_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Cell 22 voltage
| 90A7 | Pack_Fault_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Cell 23 voltage
| 90A8 | Pack_Fault_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage
| 90A9 | Pack_Fault_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | The highest voltage of the battery
| 90AA | Pack_Fault_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum battery voltage
| 90AB | Pack_Fault_Temperature1_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 1
| 90AC | Pack_Fault_Temperature2_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 2
| 90AD | Pack_Fault_Temperature3_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 3
| 90AE | Pack_Fault_Temperature4_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 4
| 90AF | Pack_Fault_Temperature_MOS | I16 | 0.1 | ℃ |  |  | R | MOS tube temperature
| 90B0 | Pack_Fault_Temperature_Env | I16 | 0.1 | ℃ |  |  | R | Ambient temperature in the battery pack
| 90B1 | Pack_Fault_Current | I16 | 0.1 | A |  |  | R | Battery pack current
| 90B2 | Pack_Fault_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity
| 90B3 | Pack_Fault_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | Full charge capacity
| 90B4 | Pack_Fault_Total_Voltage | U16 | 0.01 | V |  |  | R | Total voltage
| 90B5 | Pack_Alarm_State | U16 |  |  |  |  | R | Alarm status
| 90B6 | Pack_Protect_State | U16 |  |  |  |  | R | Protection status
| 90B7 | Pack_Fault_State | U16 |  |  |  |  | R | Fault state
90B8
90B9
90BA
90BB
90BC
90BD
90BE
90BF
Note on G1145: PF1VK175: -10000~-8000对应功率因数-1~-0.8
Note on H1145: PF1VK175: 8000~10000对应功率因数0.8~1

## Fault Addresses
Table | Byte | Bit | Field | No. | Remarks | classification
Fault1 | byte 0 | bit 0 | GridOVP | 001 | Grid over-voltage | Grid
|  | bit 1 | GridUVP | 002 | Grid undervoltage
|  | bit 2 | GridOFP | 003 | Grid Overfrequency
|  | bit 3 | GridUFP | 004 | Grid Underfrequency
|  | bit 4 | GFCI | 005 | Leakage current fault
|  | bit 5 | OVRT | 006 | High penetration error
|  | bit 6 | LVRT | 007 | Low penetration error
|  | bit 7 | IslandFault | 008 | Islanding error
| byte 1 | bit 0 | GridOVPInstant1 | 009 | Grid voltage transient value overvoltage 1
|  | bit 1 | GridOVPInstant2 | 010 | Grid voltage transient value overvoltage 2
|  | bit 2 | VGridLineFault | 011 | Grid line voltage error
|  | bit 3 | InvVoltFault | 012 | Inverter voltage error
|  | bit 4 | RefluxFault | 013 | Anti-backflow overload
|  | bit 5 | VGridUnbalance | 014 | Grid voltage unbalance
|  | bit 6 | VGridNPEOver | 015 | Zero-ground voltage too high
|  | bit 7 |  | 016
Fault2 | byte 0 | bit 0 | HwADErrIGrid | 017 | Grid current sampling error | Sampling error
|  | bit 1 | HwADErrDCI(AC) | 018 | Grid current DC component sampling error (AC side)
|  | bit 2 | HwADErrVGrid(DC) | 019 | Grid voltage sampling error (DC side)
|  | bit 3 | HwADErrVGrid(AC) | 020 | Grid voltage sampling error (AC side)
|  | bit 4 | HwGFCIFault(DC) | 021 | Leakage current sampling error (DC side)
|  | bit 5 | HwGFCIFault(AC) | 022 | Leakage current sampling error (AC side)
|  | bit 6 | HwADErrDCV | 023 | Load voltage DC component sampling error
|  | bit 7 | HwADErrIdc | 024 | DC input current sampling error
| byte 1 | bit 0 | HwADErrDCI(DC) | 025 | DC component sampling error of grid current (DC side)
|  | bit 1 | HwADErrIdcBranch | 026 | DC input branch current sampling error
|  | bit 2 |  | 027
|  | bit 3 | PIDAbnormalOut | 028 | PID abnormal output
|  | bit 4 | ConsistentGFCI | 029 | Leakage current consistency error
|  | bit 5 | ConsistentVgrid | 030 | Grid voltage consistency error
|  | bit 6 | ConsistentDCI | 031 | DCI consistency error
|  | bit 7 |  | 032
Fault3 | byte 0 | bit 0 | SpiCommFault(DC) | 033 | SPI communication error (DC side)
|  | bit 1 | SpiCommFault(AC) | 034 | SPI communication error (AC side)
|  | bit 2 | SChip_Fault | 035 | Chip error (DC side)
|  | bit 3 | MChip_Fault | 036 | Chip error (AC side)
|  | bit 4 | HwAuxPowerFault | 037 | Auxiliary power error
|  | bit 5 | InvSoftStartFail | 038 | Inverter soft start failure
|  | bit 6 | ArcShutdownAlarm | 039 | Arc shutdown protection
|  | bit 7 | LowLightChkFail | 040 | Weak light detection failure
| byte 1 | bit 0 | RelayFail | 041 | Relay detection failure | System
|  | bit 1 | IsoFault | 042 | Low insulation impedance
|  | bit 2 | PEConnectFault | 043 | Grounding error
|  | bit 3 | PvConfigError | 044 | Input mode setting error
|  | bit 4 | CTDisconnect | 045 | CT error
|  | bit 5 | ReversalConnect | 046 | Input reversal error
|  | bit 6 | ParallelFault | 047 | Parallel error
|  | bit 7 | SNTypeFault | 048 | Serial number error
Fault4 | byte 0 | bit 0 | TempErrBat | 049 | Battery temperature protection | Temperature
|  | bit 1 | TempErrHeatSink1 | 050 | Heat sink 1 temperature protection
|  | bit 2 | TempErrHeatSink2 | 051 | Heater 2 temperature protection
|  | bit 3 | TempErrHeatSink3 | 052 | Heater 3 temperature protection
|  | bit 4 | TempErrHeatSink4 | 053 | Heatsink 4 temperature protection
|  | bit 5 | TempErrHeatSink5 | 054 | Heatsink 5 temperature protection
|  | bit 6 | TempErrHeatSink6 | 055 | Radiator 6 temperature protection
|  | bit 7 |  | 056
| byte 1 | bit 0 | TempErrEnv1 | 057 | Ambient temperature 1 protection
|  | bit 1 | TempErrEnv2 | 058 | Ambient temperature 2 protection
|  | bit 2 | TempErrInv1 | 059 | Module 1 temperature protection
|  | bit 3 | TempErrInv2 | 060 | Module 2 temperature protection
|  | bit 4 | TempErrInv3 | 061 | Module 3 temperature protection
|  | bit 5 | TempDiffErrInv | 062 | Module temperature difference is too large
|  | bit 6 |  | 063
|  | bit 7 |  | 064
Fault5 | byte 0 | bit 0 | BusRmsUnbalance | 065 | Bus voltage RMS unbalance | Over and under voltage
|  | bit 1 | BusInstUnbalance | 066 | Bus voltage transient value unbalance
|  | bit 2 | BusUVP | 067 | Undervoltage of busbar during grid connection
|  | bit 3 | BusZVP | 068 | Bus bar low voltage
|  | bit 4 | PVOVP | 069 | PV overvoltage
|  | bit 5 | BatOVP | 070 | Battery over-voltage
|  | bit 6 | LLCBusOVP | 071 | LLCBus overvoltage protection
|  | bit 7 | SwBusRmsOVP | 072 | Inverter bus voltage RMS software overvoltage
| byte 1 | bit 0 | SwBusIOVP | 073 | Inverter bus voltage transient value software overvoltage
|  | bit 1 | FlyingCapOVP | 074 | Flying Cross Capacitor Overvoltage Protection
|  | bit 2 | FlyingCapUVP | 075 | Flying Cross capacitor undervoltage protection
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
Fault6 | byte 0 | bit 0 | SwBatOCP | 081 | Battery overcurrent software protection | Current
|  | bit 1 | DciOCP | 082 | Dci overcurrent protection
|  | bit 2 | SwIOCP | 083 | Output transient current protection
|  | bit 3 | SwBuckBoostOCP | 084 | BuckBoost software overcurrent
|  | bit 4 | SwAcRmsOCP | 085 | Output RMS current protection
|  | bit 5 | SwPvOCPInstant | 086 | PV instantaneous current overcurrent software protection
|  | bit 6 | IpvUnbalance | 087 | PV parallel uneven current
|  | bit 7 | IacUnbalance | 088 | Output current unbalance
| byte 1 | bit 0 | SwPvOCP | 089 | PV software overcurrent protection
|  | bit 1 | IbalanceOCP | 090 | Balanced circuit overcurrent protection
|  | bit 2 | ResOver | 091 | Resonance protection
|  | bit 3 | SwAcCBCFault | 092 | Software PWM current limit protection
|  | bit 4 | SwPvBranchOCP | 093 | PV string software overcurrent
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
Fault7 | byte 0 | bit 0 | HwLLCBusOVP | 097 | LLC bus hardware overvoltage | Hardware signal
|  | bit 1 | HwBusOVP | 098 | Inverter bus hardware overvoltage
|  | bit 2 | HwBuckBoostOCP | 099 | BuckBoost hardware overcurrent
|  | bit 3 | HwBatOCP | 100 | Battery hardware overcurrent
|  | bit 4 |  | 101
|  | bit 5 | HwPVOCP | 102 | PV hardware overcurrent
|  | bit 6 | HwACOCP | 103 | AC output hardware overcurrent
|  | bit 7 |  | 104
| byte 1 | bit 0 | MeterCommFault | 105 | Power meter error | Hardware signal reservation, overload
|  | bit 1 | SNMachineFault | 106 | Serial number model error
|  | bit 2 | HwVerError | 107 | Hardware version mismatch
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 | Overload1 | 110 | Overload protection 1
|  | bit 6 | Overload2 | 111 | Overload protection 2
|  | bit 7 | Overload3 | 112 | Overload protection 3
Fault8 | byte 0 | bit 0 | OverTempDerating | 113 | Overtemperature derating | Load reduction | This fault word is only used to generate an alarm and will not directly cause the system to enter a fault state.
|  | bit 1 | FreqDerating | 114 | Frequency down load
|  | bit 2 | FreqLoading | 115 | Frequency loading
|  | bit 3 | VoltDerating | 116 | Voltage down load
|  | bit 4 | VoltLoading | 117 | Voltage loading
|  | bit 5 |  | 118
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 | SpdFail(DC) | 121 | Lightning protection failure (DC) | Shut down
|  | bit 1 | SpdFail(AC) | 122 | Lightning protection failure (AC)
|  | bit 2 |  | 123
|  | bit 3 | BatDchgProhibit | 124 | Battery low voltage protection
|  | bit 4 | BatLowVoltShut | 125 | Battery low voltage shutdown
|  | bit 5 |  | 126 | Battery low voltage pre-alarm
|  | bit 6 |  | 127
|  | bit 7 |  | 128
Fault9 | byte 0 | bit 0 | PermHwAcOCP | 129 | Output hardware overcurrent permanent fault | Permanent
|  | bit 1 | PermBusOVP | 130 | Bus overvoltage permanent fault
|  | bit 2 | PermHwBusOVP | 131 | Bus hardware over-voltage permanent fault
|  | bit 3 | PermIpvUnbalance | 132 | PV uneven flow permanent fault
|  | bit 4 | PermEPSBatOCP | 133 | Battery overcurrent permanent fault in EPS mode
|  | bit 5 | PermAcOCPInstant | 134 | Output transient overcurrent permanent fault
|  | bit 6 | PermIacUnbalance | 135 | Output current unbalance permanent fault
|  | bit 7 | PermInvStartFail | 136 | Inverter soft start failure fault
| byte 1 | bit 0 | PermInCfgError | 137 | Input mode setting error permanent fault
|  | bit 1 | PermDCOCPInstant | 138 | Input overcurrent permanent fault
|  | bit 2 | PermHwDCOCP | 139 | Input hardware overcurrent permanent fault
|  | bit 3 | PermRelayFail | 140 | Relay permanent fault
|  | bit 4 | PermBusUnbalance | 141 | Bus unbalance permanent fault
|  | bit 5 | PermSpdFail(DC) | 142 | Lightning protection permanent fault - DC side
|  | bit 6 | PermSpdFail(AC) | 143 | Lightning protection permanent fault - AC side
|  | bit 7 |  | 144
Fault10 | byte 0 | bit 0 | USBFault | 145 | USB fault | Communication board
|  | bit 1 | WifiFault | 146 | WIFI fault
|  | bit 2 | BluetoothFault | 147 | Bluetooth fault
|  | bit 3 | RTCFault | 148 | RTC clock fault
|  | bit 4 | CommEEPROMFault | 149 | Communication board EEPROM error
|  | bit 5 | FlashFault | 150 | Communication board FLASH error
|  | bit 6 |  | 151
|  | bit 7 | SafetyVerFault | 152 | Safety regulation version error
| byte 1 | bit 0 | SCILose(DC) | 153 | SCI communication error (DC side)
|  | bit 1 | SCILose(AC) | 154 | SCI communication error (AC side)
|  | bit 2 | SCILose(Fuse) | 155 | SCI communication error (convergence board side)
|  | bit 3 | SoftVerError | 156 | Software version inconsistency
|  | bit 4 | BMS1CommFault | 157 | Lithium battery 1 communication error
|  | bit 5 | BMS2CommFault | 158 | Li-ion battery 2 communication error
|  | bit 6 | BMS3CommFault | 159 | Lithium battery 3 communication error
|  | bit 7 | BMS4CommFault | 160 | Lithium battery 4 communication failure
Fault11 | byte 0 | bit 0 | ForceShutdown | 161 | Forced shutdown | The communication board is shut down and the load is reduced
|  | bit 1 | RemoteShutdown | 162 | Remote shutdown
|  | bit 2 | Drms0Shutdown | 163 | Drms0 shutdown
|  | bit 3 |  | 164
|  | bit 4 | RemoteDerating | 165 | Remote down load
|  | bit 5 | LogicIfDerating | 166 | Logic interface down load
|  | bit 6 | AlarmAntiReflux | 167 | Anti-Reverse Flow Downgrade
|  | bit 7 |  | 168
| byte 1 | bit 0 | FanFault1 | 169 | Fan 1 failure | External components
|  | bit 1 | FanFault2 | 170 | Fan 2 failure
|  | bit 2 | FanFault3 | 171 | Fan 3 failure
|  | bit 3 | FanFault4 | 172 | Fan 4 failure
|  | bit 4 | FanFault5 | 173 | Fan 5 failure
|  | bit 5 | FanFault6 | 174 | Fan 6 failure
|  | bit 6 | FanFault7 | 175 | Fan 7 fault
|  | bit 7 | MeterCommLose | 176 | Meter communication failure
Fault12 | byte 0 | bit 0 | BMS OVP | 177 | BMS over-voltage alarm | BMS
|  | bit 1 | BMS UVP | 178 | BMS undervoltage alarm
|  | bit 2 | BMS OTP | 179 | BMS high temperature alarm
|  | bit 3 | BMS UTP | 180 | BMS low temperature alarm
|  | bit 4 | BMS OCP | 181 | BMS charge/discharge overload alarm
|  | bit 5 | BMS Short | 182 | BMS short circuit alarm
|  | bit 6 | BMS VerFault | 183 | BMS version inconsistency
|  | bit 7 | BMS CAN VerFault | 184 | BMS CAN version inconsistency
| byte 1 | bit 0 | BMS CAN VerLow | 185 | BMS CAN version is too low
|  | bit 1 |  | 186
|  | bit 2 |  | 187
|  | bit 3 |  | 188
|  | bit 4 | AFCICommLose | 189 | Arc device communication failure
|  | bit 5 | DCArcingAlarm | 190 | DC arc alarm fault
|  | bit 6 | PID_Output_Fail | 191 | PID repair failed
|  | bit 7 | PLC_Com_Fail | 192 | PLC module heartbeat loss
Fault13 | byte 0 | bit 0 | StrFuseALM1-1 | 193 | String fuse open circuit alarm 1-1 | FUSE
|  | bit 1 | StrFuseALM1-2 | 194 | String fuse open circuit alarm 1-2
|  | bit 2 | StrFuseALM2-1 | 195 | String fuse open circuit alarm 2-1
|  | bit 3 | StrFuseALM2-2 | 196 | String fuse open circuit alarm 2-2
|  | bit 4 | StrFuseALM3-1 | 197 | String fuse open circuit alarm 3-1
|  | bit 5 | StrFuseALM3-2 | 198 | String fuse open circuit alarm 3-2
|  | bit 6 | StrFuseALM4-1 | 199 | String fuse open circuit alarm 4-1
|  | bit 7 | StrFuseALM4-2 | 200 | String fuse open circuit alarm 4-2
| byte 1 | bit 0 | StrFuseALM5-1 | 201 | String fuse open circuit alarm 5-1
|  | bit 1 | StrFuseALM5-2 | 202 | String fuse open circuit alarm 5-2
|  | bit 2 | StrFuseALM6-1 | 203 | String fuse open circuit alarm 6-1
|  | bit 3 | StrFuseALM6-2 | 204 | String fuse open circuit alarm 6-2
|  | bit 4 | StrFuseALM7-1 | 205 | String fuse open circuit alarm 7-1
|  | bit 5 | StrFuseALM7-2 | 206 | String fuse open circuit alarm 7-2
|  | bit 6 | StrFuseALM8-1 | 207 | String fuse open circuit alarm 8-1
|  | bit 7 | StrFuseALM8-2 | 208 | String fuse open circuit alarm 8-2
Fault14 | byte 0 | bit 0 | StrFuseALM9-1 | 209 | String fuse open circuit alarm 9-1
|  | bit 1 | StrFuseALM9-2 | 210 | String fuse open circuit alarm 9-2
|  | bit 2 | StrFuseALM10-1 | 211 | String fuse open circuit alarm 10-1
|  | bit 3 | StrFuseALM10-2 | 212 | String fuse open circuit alarm 10-2
|  | bit 4 | StrFuseALM11-1 | 213 | String fuse open circuit alarm 11-1
|  | bit 5 | StrFuseALM11-2 | 214 | String fuse open circuit alarm 11-2
|  | bit 6 | StrFuseALM12-1 | 215 | String fuse open circuit alarm 12-1
|  | bit 7 | StrFuseALM12-2 | 216 | String fuse open circuit alarm 12-2
| byte 1 | bit 0 | StrFuseALM13-1 | 217 | String fuse open circuit alarm 13-1
|  | bit 1 | StrFuseALM13-2 | 218 | String fuse open circuit alarm 13-2
|  | bit 2 | StrFuseALM14-1 | 219 | String fuse open circuit alarm 14-1
|  | bit 3 | StrFuseALM14-2 | 220 | String fuse open circuit alarm 14-2
|  | bit 4 | StrFuseALM15-1 | 221 | String fuse open circuit alarm 15-1
|  | bit 5 | StrFuseALM15-2 | 222 | String fuse open circuit alarm 15-2
|  | bit 6 | StrFuseALM16-1 | 223 | String fuse open circuit alarm 16-1
|  | bit 7 | StrFuseALM16-2 | 224 | String fuse open circuit alarm 16-2
Fault15 | byte 0 | bit 0 | InputFuseALM0 | 225 | Battery input fuse open circuit alarm 0
|  | bit 1 | InputFuseALM1 | 226 | Battery input fuse open circuit alarm 1
|  | bit 2 | InputFuseALM2 | 227 | Battery input fuse open circuit alarm 2
|  | bit 3 | InputFuseALM3 | 228 | Battery input fuse open circuit alarm 3
|  | bit 4 | InputFuseALM4 | 229 | Battery input fuse open circuit alarm 4
|  | bit 5 | InputFuseALM5 | 230 | Battery input fuse open circuit alarm 5
|  | bit 6 | InputFuseALM6 | 231 | Battery input fuse open circuit alarm 6
|  | bit 7 | InputFuseALM7 | 232 | Battery input fuse open circuit alarm 7
| byte 1 | bit 0 | InputFuseALM8 | 233 | Battery input fuse open circuit alarm 8
|  | bit 1 | InputFuseALM9 | 234 | Battery input fuse open circuit alarm 9
|  | bit 2 | InputFuseALM10 | 235 | Battery input fuse open circuit alarm 10
|  | bit 3 | InputFuseALM11 | 236 | Battery input fuse open circuit alarm 11
|  | bit 4 | InputFuseALM12 | 237 | Battery input fuse open circuit alarm 12
|  | bit 5 | InputFuseALM13 | 238 | Battery input fuse open circuit alarm 13
|  | bit 6 | InputFuseALM14 | 239 | Battery input fuse open circuit alarm 14
|  | bit 7 | InputFuseALM15 | 240 | Battery input fuse open circuit alarm 15
Fault16 | byte 0 | bit 0 | CombinerOVGp1 | 241 |  | Confluence
|  | bit 1 | CombinerOVGp2 | 242
|  | bit 2 | CombinerOVGp3 | 243
|  | bit 3 | CombinerOVGp4 | 244
|  | bit 4 | CombinerOVGp5 | 245
|  | bit 5 | CombinerOVGp6 | 246
|  | bit 6 | CombinerOVGp7 | 247
|  | bit 7 | CombinerOVGp8 | 248
| byte 1 | bit 0 | CombinerOVGp9 | 249
|  | bit 1 | CombinerOVGp10 | 250
|  | bit 2 | CombinerOVGp11 | 251
|  | bit 3 | CombinerOVGp12 | 252
|  | bit 4 | CombinerOVGp13 | 253
|  | bit 5 | CombinerOVGp14 | 254
|  | bit 6 | CombinerOVGp15 | 255
|  | bit 7 | CombinerOVGp16 | 256
Fault17 | byte 0 | bit 0 | CombinerUVGp1 | 257 |  | Confluence
|  | bit 1 | CombinerUVGp2 | 258
|  | bit 2 | CombinerUVGp3 | 259
|  | bit 3 | CombinerUVGp4 | 260
|  | bit 4 | CombinerUVGp5 | 261
|  | bit 5 | CombinerUVGp6 | 262
|  | bit 6 | CombinerUVGp7 | 263
|  | bit 7 | CombinerUVGp8 | 264
| byte 1 | bit 0 | CombinerUVGp9 | 265
|  | bit 1 | CombinerUVGp10 | 266
|  | bit 2 | CombinerUVGp11 | 267
|  | bit 3 | CombinerUVGp12 | 268
|  | bit 4 | CombinerUVGp13 | 269
|  | bit 5 | CombinerUVGp14 | 270
|  | bit 6 | CombinerUVGp15 | 271
|  | bit 7 | CombinerUVGp16 | 272
Fault18 | byte 0 | bit 0 | CombinerOC1 | 273 |  | Confluence
|  | bit 1 | CombinerOC2 | 274
|  | bit 2 | CombinerOC3 | 275
|  | bit 3 | CombinerOC4 | 276
|  | bit 4 | CombinerOC5 | 277
|  | bit 5 | CombinerOC6 | 278
|  | bit 6 | CombinerOC7 | 279
|  | bit 7 | CombinerOC8 | 280
| byte 1 | bit 0 | CombinerOC9 | 281
|  | bit 1 | CombinerOC10 | 282
|  | bit 2 | CombinerOC11 | 283
|  | bit 3 | CombinerOC12 | 284
|  | bit 4 | CombinerOC13 | 285
|  | bit 5 | CombinerOC14 | 286
|  | bit 6 | CombinerOC15 | 287
|  | bit 7 | CombinerOC16 | 288
Fault19 | byte 0 | bit 0 | CombinerOC17 | 289 |  | Confluence
|  | bit 1 | CombinerOC18 | 290
|  | bit 2 | CombinerOC19 | 291
|  | bit 3 | CombinerOC20 | 292
|  | bit 4 | CombinerOC21 | 293
|  | bit 5 | CombinerOC22 | 294
|  | bit 6 | CombinerOC23 | 295
|  | bit 7 | CombinerOC24 | 296
| byte 1 | bit 0 | CombinerOC25 | 297
|  | bit 1 | CombinerOC26 | 298
|  | bit 2 | CombinerOC27 | 299
|  | bit 3 | CombinerOC28 | 300
|  | bit 4 | CombinerOC29 | 301
|  | bit 5 | CombinerOC30 | 302
|  | bit 6 | CombinerOC31 | 303
|  | bit 7 | CombinerOC32 | 304
Fault20 | byte 0 | bit 0 |  | 305 |  | Confluence
|  | bit 1 |  | 306
|  | bit 2 |  | 307
|  | bit 3 |  | 308
|  | bit 4 |  | 309
|  | bit 5 |  | 310
|  | bit 6 |  | 311
|  | bit 7 |  | 312
| byte 1 | bit 0 |  | 313
|  | bit 1 |  | 314
|  | bit 2 |  | 315
|  | bit 3 |  | 316
|  | bit 4 |  | 317
|  | bit 5 |  | 318
|  | bit 6 |  | 319
|  | bit 7 |  | 320
Fault21 | byte 0 | bit 0 |  | 321 |  | Confluence
|  | bit 1 |  | 322
|  | bit 2 |  | 323
|  | bit 3 |  | 324
|  | bit 4 |  | 325
|  | bit 5 |  | 326
|  | bit 6 |  | 327
|  | bit 7 |  | 328
| byte 1 | bit 0 |  | 329
|  | bit 1 |  | 330
|  | bit 2 |  | 331
|  | bit 3 |  | 332
|  | bit 4 |  | 333
|  | bit 5 |  | 334
|  | bit 6 |  | 335
|  | bit 7 |  | 336
Fault22 | byte 0 | bit 0 | CombinerRefluxFault1 | 337 |  | Confluence
|  | bit 1 | CombinerRefluxFault2 | 338
|  | bit 2 | CombinerRefluxFault3 | 339
|  | bit 3 | CombinerRefluxFault4 | 340
|  | bit 4 | CombinerRefluxFault5 | 341
|  | bit 5 | CombinerRefluxFault6 | 342
|  | bit 6 | CombinerRefluxFault7 | 343
|  | bit 7 | CombinerRefluxFault8 | 344
| byte 1 | bit 0 | CombinerRefluxFault9 | 345
|  | bit 1 | CombinerRefluxFault10 | 346
|  | bit 2 | CombinerRefluxFault11 | 347
|  | bit 3 | CombinerRefluxFault12 | 348
|  | bit 4 | CombinerRefluxFault13 | 349
|  | bit 5 | CombinerRefluxFault14 | 350
|  | bit 6 | CombinerRefluxFault15 | 351
|  | bit 7 | CombinerRefluxFault16 | 352
Fault23 | byte 0 | bit 0 | CombinerRefluxFault17 | 353 |  | Confluence
|  | bit 1 | CombinerRefluxFault18 | 354
|  | bit 2 | CombinerRefluxFault19 | 355
|  | bit 3 | CombinerRefluxFault20 | 356
|  | bit 4 | CombinerRefluxFault21 | 357
|  | bit 5 | CombinerRefluxFault22 | 358
|  | bit 6 | CombinerRefluxFault23 | 359
|  | bit 7 | CombinerRefluxFault24 | 360
| byte 1 | bit 0 | CombinerRefluxFault25 | 361
|  | bit 1 | CombinerRefluxFault26 | 362
|  | bit 2 | CombinerRefluxFault27 | 363
|  | bit 3 | CombinerRefluxFault28 | 364
|  | bit 4 | CombinerRefluxFault29 | 365
|  | bit 5 | CombinerRefluxFault30 | 366
|  | bit 6 | CombinerRefluxFault31 | 367
|  | bit 7 | CombinerRefluxFault32 | 368
Fault24 | byte 0 | bit 0 |  | 369 |  | Confluence
|  | bit 1 |  | 370
|  | bit 2 |  | 371
|  | bit 3 |  | 372
|  | bit 4 |  | 373
|  | bit 5 |  | 374
|  | bit 6 |  | 375
|  | bit 7 |  | 376
| byte 1 | bit 0 |  | 377
|  | bit 1 |  | 378
|  | bit 2 |  | 379
|  | bit 3 |  | 380
|  | bit 4 |  | 381
|  | bit 5 |  | 382
|  | bit 6 |  | 383
|  | bit 7 |  | 384
Fault25 | byte 0 | bit 0 |  | 385 |  | Confluence
|  | bit 1 |  | 386
|  | bit 2 |  | 387
|  | bit 3 |  | 388
|  | bit 4 |  | 389
|  | bit 5 |  | 390
|  | bit 6 |  | 391
|  | bit 7 |  | 392
| byte 1 | bit 0 |  | 393
|  | bit 1 |  | 394
|  | bit 2 |  | 395
|  | bit 3 |  | 396
|  | bit 4 |  | 397
|  | bit 5 |  | 398
|  | bit 6 |  | 399
|  | bit 7 |  | 400
Fault26 | byte 0 | bit 0 | AFCI0 | 401 | Arc fault | AFCI
|  | bit 1 | AFCI1 | 402 | Arc fault
|  | bit 2 | AFCI2 | 403 | Arc fault
|  | bit 3 | AFCI3 | 404 | Arc fault
|  | bit 4 | AFCI4 | 405 | Arc fault
|  | bit 5 | AFCI5 | 406 | Arc fault
|  | bit 6 | AFCI6 | 407 | Arc fault
|  | bit 7 | AFCI7 | 408 | Arc fault
| byte 1 | bit 0 | AFCI8 | 409 | Arc fault
|  | bit 1 | AFCI9 | 410 | Arc fault
|  | bit 2 | AFCI10 | 411 | Arc fault
|  | bit 3 | AFCI11 | 412 | Arc fault
|  | bit 4 | AFCI12 | 413 | Arc fault
|  | bit 5 | AFCI13 | 414 | Arc fault
|  | bit 6 | AFCI14 | 415 | Arc fault
|  | bit 7 | AFCI15 | 416 | Arc fault
Fault27 | byte 0 | bit 0 | AFCI16 | 417 | Arc fault | AFCI
|  | bit 1 | AFCI17 | 418 | Arc fault
|  | bit 2 | AFCI18 | 419 | Arc fault
|  | bit 3 | AFCI19 | 420 | Arc fault
|  | bit 4 | AFCI20 | 421 | Arc fault
|  | bit 5 | AFCI21 | 422 | Arc fault
|  | bit 6 | AFCI22 | 423 | Arc fault
|  | bit 7 | AFCI23 | 424 | Arc fault
| byte 1 | bit 0 | AFCI24 | 425 | Arc fault
|  | bit 1 | AFCI25 | 426 | Arc fault
|  | bit 2 | AFCI26 | 427 | Arc fault
|  | bit 3 | AFCI27 | 428 | Arc fault
|  | bit 4 | AFCI28 | 429 | Arc fault
|  | bit 5 | AFCI29 | 430 | Arc fault
|  | bit 6 | AFCI30 | 431 | Arc fault
|  | bit 7 | AFCI31 | 432 | Arc fault

## Status Information Sheet
Table | Byte | Bit | 位字段 | 编号 | 备注
State1 | byte 0 | bit 0 | Grid low voltage down load | 001 | 电网低压降载
|  | bit 1 | Over-temperature down load | 002 | 过温降载
|  | bit 2 | Bus over-voltage derating | 003 | 母线过压降载
|  | bit 3 | Reactive power limit active power | 004 | 无功限有功
|  | bit 4 | Command active load reduction | 005 | 指令有功降载
|  | bit 5 | DRMs down load | 006 | DRMs降载
|  | bit 6 | Anti-reflux load shedding | 007 | 防逆流降载
|  | bit 7 | Remote active power control | 008 | 远程有功控制
| byte 1 | bit 0 | Over-undervoltage load shedding | 009 | 过欠压降载
|  | bit 1 | Overfrequency derate | 010 | 过频降载
|  | bit 2 | Under frequency loading | 011 | 欠频加载
|  | bit 3 | Internal load shedding | 012 | 内部降载
|  | bit 4 |  | 013
|  | bit 5 |  | 014
|  | bit 6 |  | 015
|  | bit 7 |  | 016
State2 | byte 0 | bit 0 | Remote PF control | 017 | 远程PF控制
|  | bit 1 | Remote reactive power control | 018 | 远程无功控制
|  | bit 2 | Independent reactive power control | 019 | 独立无功控制
|  | bit 3 |  | 020
|  | bit 4 |  | 021
|  | bit 5 |  | 022
|  | bit 6 |  | 023
|  | bit 7 |  | 024
| 0 | bit 0 | Forced shutdown | 025 | 强制关机
|  | bit 1 | Remote shutdown | 026 | 远程关机
|  | bit 2 | DRMs0 Shutdown | 027 | DRMs0关机
|  | bit 3 |  | 028
|  | bit 4 |  | 029
|  | bit 5 |  | 030
|  | bit 6 |  | 031
|  | bit 7 |  | 032
State3 | byte 0 | bit 0 |  | 033
|  | bit 1 |  | 034
|  | bit 2 |  | 035
|  | bit 3 |  | 036
|  | bit 4 |  | 037
|  | bit 5 |  | 038
|  | bit 6 |  | 039
|  | bit 7 |  | 040
| byte 1 | bit 0 |  | 041
|  | bit 1 |  | 042
|  | bit 2 |  | 043
|  | bit 3 |  | 044
|  | bit 4 |  | 045
|  | bit 5 |  | 046
|  | bit 6 |  | 047
|  | bit 7 |  | 048
State4 | byte 0 | bit 0 |  | 049
|  | bit 1 |  | 050
|  | bit 2 |  | 051
|  | bit 3 |  | 052
|  | bit 4 |  | 053
|  | bit 5 |  | 054
|  | bit 6 |  | 055
|  | bit 7 |  | 056
| byte 1 | bit 0 |  | 057
|  | bit 1 |  | 058
|  | bit 2 |  | 059
|  | bit 3 |  | 060
|  | bit 4 |  | 061
|  | bit 5 |  | 062
|  | bit 6 |  | 063
|  | bit 7 |  | 064
State5 | byte 0 | bit 0 |  | 065
|  | bit 1 |  | 066
|  | bit 2 |  | 067
|  | bit 3 |  | 068
|  | bit 4 |  | 069
|  | bit 5 |  | 070
|  | bit 6 |  | 071
|  | bit 7 |  | 072
| byte 1 | bit 0 |  | 073
|  | bit 1 |  | 074
|  | bit 2 |  | 075
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
State6 | byte 0 | bit 0 | RemoteDerating | 081 | 远程降载使能
|  | bit 1 | LogicIfDerating | 082 | 逻辑接口降载使能
|  | bit 2 | AlarmAntiReflux | 083 | 防逆流降载使能
|  | bit 3 |  | 084
|  | bit 4 |  | 085
|  | bit 5 |  | 086
|  | bit 6 |  | 087
|  | bit 7 |  | 088
| byte 1 | bit 0 |  | 089
|  | bit 1 |  | 090
|  | bit 2 |  | 091
|  | bit 3 |  | 092
|  | bit 4 |  | 093
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
State7 | byte 0 | bit 0 |  | 097
|  | bit 1 |  | 098
|  | bit 2 |  | 099
|  | bit 3 |  | 100
|  | bit 4 |  | 101
|  | bit 5 |  | 102
|  | bit 6 |  | 103
|  | bit 7 |  | 104
| byte 1 | bit 0 |  | 105
|  | bit 1 |  | 106
|  | bit 2 |  | 107
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 |  | 110
|  | bit 6 |  | 111
|  | bit 7 |  | 112
State8 | byte 0 | bit 0 |  | 113
|  | bit 1 |  | 114
|  | bit 2 |  | 115
|  | bit 3 |  | 116
|  | bit 4 |  | 117
|  | bit 5 |  | 118
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 |  | 121
|  | bit 1 |  | 122
|  | bit 2 |  | 123
|  | bit 3 |  | 124
|  | bit 4 |  | 125
|  | bit 5 |  | 126
|  | bit 6 |  | 127
|  | bit 7 |  | 128
State9 | byte 0 | bit 0 |  | 129
|  | bit 1 |  | 130
|  | bit 2 |  | 131
|  | bit 3 |  | 132
|  | bit 4 |  | 133
|  | bit 5 |  | 134
|  | bit 6 |  | 135
|  | bit 7 |  | 136
| byte 1 | bit 0 |  | 137
|  | bit 1 |  | 138
|  | bit 2 |  | 139
|  | bit 3 |  | 140
|  | bit 4 |  | 141
|  | bit 5 |  | 142
|  | bit 6 |  | 143
|  | bit 7 |  | 144

## PCU fault bit description
Warning1 | bit | ID | 故障 | 注释
| 0 | 800
| 1 | 801 | IschgSoftStartFail | 充电软起动失败
| 2 | 802 | IsdchgSoftStartFail | 放电软起失败
| 3 | 803 | Fan1Fault | 风扇1故障
| 4 | 804 | Fan2Fault | 风扇2故障
| 5 | 805 | Fan3Fault | 风扇3故障
| 6 | 806 | Fan4Fault | 风扇4故障
| 7 | 807 | PCU VerFault | PCU版本不一致
| 8 | 808 | HS1HighTempWarning | 散热器1过温告警
| 9 | 809 | EnvHighTempWarning | 环境温度过温告警
| 10 | 810 | HS2HighTempWarning | 散热器2过温告警
| 11 | 811
| 12 | 812
| 13 | 813 | StopChgWarning | 禁止充电告警
| 14 | 814 | StopDchgWarning | 禁止放电告警
| 15 | 815 | BatUnbalancedWarning | 电池不均衡告警
Warning2 | 0 | 816 | BusAvgOVWarning | 母线过压告警
| 1 | 817 | BusAvgUVWarning | 母线欠压告警
| 2 | 818 | BatAvgOVWarning | 电池过压告警
| 3 | 819 | BatAvgUVWarning | 电池欠压告警
| 4 | 820
| 5 | 821
| 6 | 822
| 7 | 823
| 8 | 824
| 9 | 825
| 11 | 827
| 12 | 828
| 13 | 829
| 14 | 830
| 15 | 831
Warning3 | 0 | 832
| 1 | 833
| 2 | 834
| 3 | 835
| 4 | 836
| 5 | 837
| 6 | 838
| 7 | 839
| 8 | 840
| 9 | 841
| 10 | 842
| 11 | 843
| 12 | 844
| 13 | 845
Warning4 | 0 | 848
| 1 | 849
| 2 | 850
| 3 | 851
| 4 | 852
| 5 | 853
| 6 | 854
| 7 | 855
| 8 | 856
| 9 | 857
| 10 | 858
| 11 | 859
| 12 | 860
| 13 | 861
| 14 | 862
| 15 | 863
Fault1 | 0 | 864 | HS1OverTempFault | 散热器1过温保护
| 1 | 865 | OverTempFault_Env | 环境温度过温保护
| 2 | 866 | SciCommFault | Sci通信故障
| 3 | 867 | Can1CommFault | Can1通信故障
| 4 | 868 | Relay1Fail | 继电器1故障
| 5 | 869 | HS2OverTempFault | 散热器2过温保护
| 6 | 870 | Can2CommFault | Can2通信故障
| 7 | 871 | Relay2Fail | 继电器2故障
| 8 | 872 | SwBusInstantOVP | 母线软件过压
| 9 | 873 | SwBusInstantUVP | 母线软件欠压
| 10 | 874 | SwBatInstantOVP | 电池软件过压
| 11 | 875 | SwBatInstantUVP | 电池软件欠压
| 12 | 876 | SwBatInstantOCP | 电池软件过流
| 13 | 877 | FlyingCap1OVP | 飞跨电容1过压
| 14 | 878 | FlyingCap2OVP | 飞跨电容2过压
| 15 | 879 | HwOCP | 硬件过流
Fault2 | 0 | 880 | unrecoverBusAvgOV | 永久母线过压
| 1 | 881 | unrecoverBatAvgUV | 永久电池欠压
| 2 | 882 | unrecoverOCPInstant | 永久过流
| 3 | 883 | unrecoverHwOCP | 永久硬件过流
| 4 | 884 | FlyingCap3OVP | 飞跨电容3过压
| 5 | 885 | FlyingCap4OVP | 飞跨电容4过压
| 6 | 886 | FlyingCap1UVP | 飞跨电容1欠压
| 7 | 887 | FlyingCap2UVP | 飞跨电容2欠压
| 8 | 888 | unrecoverRelay1Fail | 继电器1永久故障
| 9 | 889 | unrecoverRelay2Fail | 继电器2永久故障
| 10 | 890 | FlyingCap3UVP | 飞跨电容3欠压
| 11 | 891 | FlyingCap4UVP | 飞跨电容4欠压
| 12 | 892
| 13 | 893
| 14 | 894
| 15 | 895
| 13 | 893
| 14 | 894 | unrecoverBatActFail | 永久电池激活失败
| 15 | 895 | unrecoverBusRPP | 永久性BUS反接
Fault3 | 0 | 896 | BatteryStateErr | 电池状态错误
| 1 | 897 | PWMModeErr | PWM模式错误
| 2 | 898 | BMSVerionErr | BMS版本错误
| 3 | 899 | BMSOVOCP | BMS过压过流故障
| 4 | 900 | SwBatAvgOCP | 电池平均值过流保护
| 5 | 901 | SwAvgOverloadP | 平均值过载保护
| 6 | 902
| 7 | 903 | SwCBCOCP | 软件CBC过流保护
| 8 | 904
| 9 | 905
| 10 | 906
| 11 | 907
| 12 | 908
| 13 | 909
| 14 | 910
| 15 | 911
Fault4 | 0 | 912
| 1 | 913
| 2 | 914
| 3 | 915
| 4 | 916
| 5 | 917
| 6 | 918
| 7 | 919
| 8 | 920
| 9 | 921
| 10 | 922
| 11 | 923
| 12 | 924
| 13 | 925
| 14 | 926
| 15 | 927

## BDU Failure Information
Fault1 | bit | ID | 故障 | 注释
| 0 | 928 | Battery reverse connection
| 1 | 929 | Fuse fault
| 2 | 930
| 3 | 931
| 4 | 932
| 5 | 933
| 6 | 934
| 7 | 935
| 8 | 936
| 9 | 937
| 10 | 938
| 11 | 939
| 12 | 940
| 13 | 941
| 14 | 942
| 15 | 943

## Version
Modified date | Address | Modification description
2020-05-23 | 0x0940 | Add Bit4
| 0x0404 | Add 2 new status descriptions
| 0x09C0 | Add Bit3
| 0x09DB-0x09DE | Add parameters
| 0x2006 | Update value definition description
2020-06-03 | 0x102D | Add CT automatic calibration register
2020-06-10 | 0x0940 | Add Bit5
2020-06-29 | 0x0914-0x0915 | Add parameters
| Fault2-byte1-bit6 | Add fault
| Fault3-byte1-bit6 | Add fault
2020-08-31 | 0x1046 | Add battery protocol type
| 0x1038 | Add address
| 0xA07C-0xA07F | Add address
| Fault3-byte0-bit5 | Add InverterSoftStartFail
| Fault3-byte1-bit7 | Add SNTypeFault
| Fault9-byte1-bit5 | Add unrecoverSpdFail(DC)
| Fault9-byte1-bit6 | Add unrecoverSpdFail(AC)
| Fault2-byte0-bit1 | Modify fault name
| Fault2-byte1-bit0 | Add HwADFaultDCI(DC)
| Fault2-byte1-bit1 | Add HwADFaultIdcBranch
| Fault10-byte1-bit4 | Modify fault name
| Fault10-byte1-bit5 | Add BMS2CommunicatonFault
| Fault10-byte1-bit6 | Add BMS3CommunicatonFault
| Fault10-byte1-bit7 | Add BMS4CommunicatonFault
| Fault10-byte0-bit7 | Add SafetyVerFault
2020-09-04 | 0x803C-0x803F | Add address
| 0x9000-0x9FFF | Add BMS transparent transmission area
| 0x06D1-0x06E2 | Add address
| Fault5-byte1-bit1 | Add FlyingCapOVP
2020-10-13 | 0x08C8-0x08CC | Add safety parameters
| 0x0A04-0x0A05 | Add safety parameters
| 0x1050 | Voltage accuracy problem correction
2020-10-30 | 0x9000-0x9FFF | New package ID in the real-time data section of the BMS transparent transmission area
| 0x4B0-0x4B9 | Add address
| 0x522-0x527 | Add address
| Fault11-byte1-bit7 | Add fault
2020-11-16 | 0x1039-0x103D | Add address
2020-12-02 | 0x0901，0x0A03 | Update the value range of the original address
| 0x1046 | Update the value range of the original address
| 0x1052 | Add battery parameter address
| 0x1054-0x1056 | Add battery parameter address
| 0x1023 | Update the value range of the original address
| 0x1024 | Original address unit update
| 0x1084-0x108C | Add arc configuration address
| 0xA070-0xA075 | Add address
| 0x0780-0x07BF | Add arc real-time information area
| 0x2007-0x200B | Add new safety country name address
| 0x0432-0x043A | Add fault information address
| Fault6-byte1-bit0 | Add SwPvOCP
| Fault26/27 | Add AFCI fault
2021-01-27 | 0x9005 | Date register type problem fixed
| 0x9051-0x906A, 0x9079, 0x9091-0x90AA, 0x90B4 | Accuracy change
| 0x907A | Add address
| 0x1105-0x110B | Add address
| 0x04BA-0x04BC | Add address
| 0x108D-0x108E | Add address
| Fault11-byte1-bit6 | Add FanFault7
| Fault12-byte0-bit6 | Add BMS VerFault
| Fault12-byte0-bit7 | Add BMS CAN VerFault
| Fault12-byte1-bit0 | Add BMS CAN VerLow
| Fault12-byte1-bit4 | Add AFCICommLose
| Fault12-byte1-bit5 | Add DCArcingAlarmFault
2021-02-05 | Fault7-byte1-bit0 | Add MeterCommFault
2021-02-16 | 0x118D-0x1190, 0x1197-0x119A, 0x11A1-0x11A4 | Data type update
| 0x1035 | Update the register value range and value definition
| Fault6-byte1-bit1 | Add IbalanceOCP
| 0x1024 | Fix the accuracy problem
2021-03-16 | Fault1-byte1-bit3 | Field name correction
| Fault1-byte1-bit4 | Added anti-backflow overload fault
| Fault8-byte1-bit3 | Field name correction
| 0x460-0x465 | Added safety version number register
| 0x0951-0x0960 | Add new safety parameter address
| 0x0980 | Added bit field definition to the original address
| 0x0981 | Maximum and minimum value corrections, please check the remarks
| 0x0982 | Maximum and minimum value corrections, please check the remarks
| 0x0993 | Update the original address field, unit, and remarks
| 0x0995 | Original address lot, remarks update
| 0x0996 | Update the original address field, type, remarks
| 0x09A1 | New safety parameter address
| 0x09C0 | Added bit field definition to the original address
| 0x0A00 | Added bit field definition to the original address
2021-06-19 | 0x05C4 | Add the total PV power address
| 0x0667-0x0669 | Add battery summary information address
| 0x0916 | Add the voltage drop time address
| 0x0940 | Add Bit6
| 0x0961-0x0962 | Add frequency address of over and under frequency power crossing point
| 0x1060 | Add PCC power acquisition device configuration address
| Fault4-byte1-bit5 | Increase the fault bit
2021-08-03 | 0x1098-0x109C | Add PID configuration address
| 0x110F | Add PID control address
| Fault12-byte1-bit6 | Add fault
2021-08-11 | 0x044C | Change from reserved address to valid serial number address
| 0x0470-0x0476 | Added 2 valid serial number addresses, and 5 reserved addresses
| 0x10A0-0x10A1 | Add PLC enable and configuration address
| 0x10A5-0x10A6 | Added BLE enable and configuration address
| 0x10B0-0x10A4 | Modify PID enable and configuration address
| 0x8027 | Change from reserved address to valid serial number address
| 0x8028-0x802E | Added 2 factory effective serial number addresses, and 5 reserved addresses
| 0x802F-0x8032 | Newly added peripheral configuration address and peripheral configuration BIT correspondence table
| 0xA06A | Add remote reset command
| Fault12-byte1-bit7 | Added PLC heartbeat failure
2021-08-31 | 0x1108 | Change the address data type to signed
| Fault13、Fault14 | Alarm name change
| 0x0040-0x0043 | Add agreement "general" area
| 0x0044 | Add protocol version number
2021-09-06 | Fault8-byte1-bit0 Fault8-byte1-bit1 | Add lightning protection failure (DC) and lightning protection failure (AC)
| 0x0044 | Update protocol version definition
| 0x0045-0x0047 | Add chipset code
2021-10-11 | 0x0940 | Add Bit7 definition
2021-11-03 | 0x1023 | Add mode definition: phase power mode
| 0x1034 | Language definition
| 0x1061 | Add resonance detection sensitivity register
| 0x1110 | Add mode definition: off-grid mode
| 0x1144-0x1146 | Added off-grid mode register
| 0x203D-0x203F | Add target chip definition: PCU (Power Control Unit) and BMS (Battery Management System)
| 0x7000-0x707F | Add ODM data customization area
| ID91 | Add resonance protection ID
| ID106 | Add serial number model error ID
2021-12-08 | 0x8020 | Address misalignment problem fixed
| 0x1051 | Register definition update
| 0x1057-0x105A | Add lead-acid battery related registers
| 0x100C | Register definition update
2021-12-27 | Fault1-byte1-bit5 | Add voltage unbalance fault
| Fault3-byte0-bit6 | Add arc protection
| Fault3-byte0-bit7 | Add weak light detection fault
| Fault6-byte1-bit2 | Change to resonance protection
| Fault6-byte1-bit3 | Add anchor current limit protection
| Fault7-byte1-bit1 | Add serial number model fault
| Fault12-byte1-bit5 | Remove arc alarm
| PCU故障位说明 | Add fault description page
| 0x0404 | Add new status
| 0x0466-0x046A | Add AFCI version
| 0x0510、0x0518、0x0520 | Modify the field for emergency load voltage
| 0x06E3-0x06EC | Add internal information register
| 0x0744-0x0763 | Add group string 3 and 4 way current
| 0x0784-0x07A1 | Modify arc pull information field
| 0x1046 | Update Register Definition
| 0x1085-0x1092 | Modify arc configuration field
| 0x1110 | Add mode definition: generator mode
| 0x2039-0x203C | New register support one-to-many upgrade and silent download
| 0x6000-0x6FFF | New PCU data area
| 0x7000 | Update Definition

## Translate
中文 | 英文
DRMs0关机 | DRMs0 Shutdown
DRMs降载 | DRMs down load
PCU版本不一致 | PCU version inconsistency
PID异常输出 | PID abnormal output
PV支路软件过流 | PV string software overcurrent
R相应急负载电压 | R corresponding emergency load voltage
S相应急负载电压 | S corresponding emergency load voltage
T相应急负载电压 | T corresponding emergency load voltage
变更为谐振保护 | Change to resonance protection
充电软起动失败 | Charge soft start failure
地址错位问题修复 | Address misalignment problem fixed
电池不均衡告警 | Battery unbalance alarm
电池过压告警 | Battery over-voltage alarm
电池接反 | Battery reverse connection
电池欠压告警 | Battery undervoltage alarm
电弧关机保护 | Arc shutdown protection
电网低压降载 | Grid low voltage down load
电网电压不平衡 | Grid voltage unbalance
独立无功控制 | Independent reactive power control
防逆流降载 | Anti-reflux load shedding
放电软起失败 | Discharge soft start failure
风扇1故障 | Fan 1 failure
风扇2故障 | Fan 2 failure
风扇3故障 | Fan 3 failure
风扇4故障 | Fan 4 failure
更新定义 | Update Definition
更新寄存器定义 | Update Register Definition
过频降载 | Overfrequency derate
过欠压降载 | Over-undervoltage load shedding
过温降载 | Over-temperature down load
环境温度过温告警 | Ambient temperature over-temperature alarm
寄存器定义更新 | Register definition update
禁止充电告警 | Prohibit charging alarm
禁止放电告警 | Prohibit discharge alarm
零地电压过高 | Zero-ground voltage too high
母线过压告警 | Bus over-voltage alarm
母线过压降载 | Bus over-voltage derating
母线欠压告警 | Bus undervoltage alarm
内部降载 | Internal load shedding
逆变软启失败故障 | Inverter soft start failure fault
欠频加载 | Under frequency loading
强制关机 | Forced shutdown
熔断故障 | Fuse fault
软件逐波限流保护 | Software PWM current limit protection
弱光检测失败 | Weak light detection failure
散热器1过温告警 | Heatsink 1 over-temperature alarm
散热器2过温告警 | Heatsink 2 over temperature alarm
删除电弧报警 | Remove arc alarm
无功限有功 | Reactive power limit active power
新增PCU数据区 | New PCU data area
新增寄存器支持一对多升级和静默下载 | New register support one-to-many upgrade and silent download
修改电弧配置字段 | Modify arc configuration field
修改拉弧信息字段 | Modify arc pull information field
修改字段为应急负载电压 | Modify the field for emergency load voltage
硬件版本不匹配 | Hardware version mismatch
远程PF控制 | Remote PF control
远程关机 | Remote shutdown
远程无功控制 | Remote reactive power control
远程有功控制 | Remote active power control
增加AFCI版本 | Add AFCI version
增加电弧保护 | Add arc protection
增加电压不平衡故障 | Add voltage unbalance fault
增加故障说明页 | Add fault description page
增加模式定义：发电机模式 | Add mode definition: generator mode
增加内部信息寄存器 | Add internal information register
增加铅酸电池相关寄存器 | Add lead-acid battery related registers
增加弱光检测故障 | Add weak light detection fault
增加新状态 | Add new status
增加序列号机型故障 | Add serial number model fault
增加主播限流保护 | Add anchor current limit protection
增加组串3、4路电流 | Add group string 3 and 4 way current
指令有功降载 | Command active load reduction